## Sheet1
id | register | name | description | system_category | category | view | sampling | read | write | minvalue | maxvalue | unit | offset | addition | mask | value | length | general_icon | alarm | metadata | l10n | tags | type | parameter_write_byte_position | mqtt | json | current_value | current_error_status | notes
1 | 1 | Temp_Imp | Temperatura Impulsion General | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | -50 | 150 | °C | 0.1 | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
2 | 2 | Temp_Ret | Temperatura Retorno General | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | -50 | 150 | °C | 0.1 | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
3 | 3 | Temp_Imp_2 | Temperatura Impulsion General 2 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | -50 | 150 | °C | 0.1 | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
4 | 4 | Temp_Ret_2 | Temperatura Retorno General 2 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | -50 | 150 | °C | 0.1 | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
5 | 5 | SP_AL_NO_WATER_FLOW | Setpoint - Alarma No water Flow | SET_POINT | DEFAULT | simple | 300 | 3 | 6 | 0 | 9.9 | barg | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
6 | 100 | Temp_Imp_G1 | Temperatura Impulsion Grupo 1 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | -50 | 150 | °C | 0.1 | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
7 | 101 | Temp_Ret_G1 | Temperatura Retorno Grupo 1 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | -50 | 150 | °C | 0.1 | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
8 | 102 | Pres_Imp_G1 | Presion Impulsion Grupo 1 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | -99.9 | 99.9 | barg | 0.1 | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
9 | 103 | Pres_Ret_G1 | Presion Retorno Grupo 1 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | -99.9 | 99.9 | barg | 0.1 | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
10 | 104 | PDiferG1 | Presion Diferencial Grupo 1 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | -99.9 | 99.9 | barg | 0.1 | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
11 | 105 | Consigna_Presion_G1 | Consigna Presion Grupo 1 | SET_POINT | DEFAULT | simple | 300 | 3 | 6 | 0 | 3276.7 | barg | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
12 | 106 | LecturaPresion_B1_G1 | Presion bomba 1 grupo 1 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 3276.7 | barg | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
13 | 107 | LecturaPresion_B2_G1 | Presion bomba 2 grupo 1 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 3276.7 | barg | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
14 | 108 | LecturaPresion_B3_G1 | Presion bomba 3 grupo 1 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 3276.7 | barg | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
15 | 109 | Frecuencia_conv | Frecuencia actual en Hz | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | Hz | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
16 | 110 | Intensidad_conv | Intensidad actual en A | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | A | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
17 | 111 | Potencia_conv | Potencia actual en KW | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | kw | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
18 | 112 | Frecuencia_conv_2 | Frecuencia actual en Hz | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | Hz | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
19 | 113 | Intensidad_conv_2 | Intensidad actual en A | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | A | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
20 | 114 | Potencia_conv_2 | Potencia actual en KW | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | kw | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
21 | 115 | Frecuencia_conv_3 | Frecuencia actual en Hz | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | Hz | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
22 | 116 | Intensidad_conv_3 | Intensidad actual en A | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | A | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
23 | 117 | Potencia_conv_3 | Potencia actual en KW | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | kw | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
24 | 200 | Temp_Imp_G2 | Temperatura Impulsion Grupo 2 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | -50 | 150 | °C | 0.1 | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
25 | 201 | Temp_Ret_G2 | Temperatura Retorno Grupo 2 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | -50 | 150 | °C | 0.1 | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
26 | 202 | Pres_Imp_G2 | Presion Impulsion Grupo 2 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | -99.9 | 99.9 | barg | 0.1 | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
27 | 203 | Pres_Ret_G2 | Presion Retorno Grupo 2 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | -99.9 | 99.9 | barg | 0.1 | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
28 | 204 | PDiferG2 | Presion Diferencial Grupo 2 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | -99.9 | 99.9 | barg | 0.1 | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
29 | 205 | Consigna_Presion_G2 | Consigna Presion Grupo 2 | SET_POINT | DEFAULT | simple | 300 | 3 | 6 | 0 | 3276.7 | barg | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
30 | 206 | LecturaPresion_B1_G2 | Presion bomba 1 grupo 2 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 3276.7 | barg | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
31 | 207 | LecturaPresion_B2_G2 | Presion bomba 2 grupo 2 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 3276.7 | barg | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
32 | 208 | LecturaPresion_B3_G2 | Presion bomba 3 grupo 2 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 3276.7 | barg | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
33 | 209 | Frecuencia_conv_4 | Frecuencia actual en Hz | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | Hz | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
34 | 210 | Intensidad_conv_4 | Intensidad actual en A | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | A | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
35 | 211 | Potencia_conv_4 | Potencia actual en KW | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | kw | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
36 | 212 | Frecuencia_conv_5 | Frecuencia actual en Hz | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | Hz | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
37 | 213 | Intensidad_conv_5 | Intensidad actual en A | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | A | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
38 | 214 | Potencia_conv_5 | Potencia actual en KW | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | kw | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
39 | 215 | Frecuencia_conv_6 | Frecuencia actual en Hz | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | Hz | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
40 | 216 | Intensidad_conv_6 | Intensidad actual en A | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | A | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
41 | 217 | Potencia_conv_6 | Potencia actual en KW | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | kw | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
42 | 300 | Temp_Imp_G3 | Temperatura Impulsion Grupo 3 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | -50 | 150 | °C | 0.1 | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
43 | 301 | Temp_Ret_G3 | Temperatura Retorno Grupo 3 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | -50 | 150 | °C | 0.1 | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
44 | 302 | Pres_Imp_G3 | Presion Impulsion Grupo 3 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | -99.9 | 99.9 | barg | 0.1 | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
45 | 303 | Pres_Ret_G3 | Presion Retorno Grupo 3 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | -99.9 | 99.9 | barg | 0.1 | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
46 | 304 | PDiferG3 | Presion Diferencial Grupo 3 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | -99.9 | 99.9 | barg | 0.1 | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
47 | 305 | Consigna_Presion_G3 | Consigna Presion Grupo 3 | SET_POINT | DEFAULT | simple | 300 | 3 | 6 | 0 | 3276.7 | barg | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
48 | 306 | LecturaPresion_B1_G3 | Presion bomba 1 grupo 3 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 3276.7 | barg | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
49 | 307 | LecturaPresion_B2_G3 | Presion bomba 2 grupo 3 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 3276.7 | barg | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
50 | 308 | LecturaPresion_B3_G3 | Presion bomba 3 grupo 3 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 3276.7 | barg | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
51 | 309 | Frecuencia_conv_7 | Frecuencia actual en Hz | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | Hz | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
52 | 310 | Intensidad_conv_7 | Intensidad actual en A | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | A | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
53 | 311 | Potencia_conv_7 | Potencia actual en KW | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | kw | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
54 | 312 | Frecuencia_conv_8 | Frecuencia actual en Hz | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | Hz | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
55 | 313 | Intensidad_conv_8 | Intensidad actual en A | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | A | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
56 | 314 | Potencia_conv_8 | Potencia actual en KW | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | kw | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
57 | 315 | Frecuencia_conv_9 | Frecuencia actual en Hz | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | Hz | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
58 | 316 | Intensidad_conv_9 | Intensidad actual en A | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | A | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
59 | 317 | Potencia_conv_9 | Potencia actual en KW | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | kw | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
60 | 400 | Temp_Imp_G4 | Temperatura Impulsion Grupo 4 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | -50 | 150 | °C | 0.1 | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
61 | 401 | Temp_Ret_G4 | Temperatura Retorno Grupo 4 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | -50 | 150 | °C | 0.1 | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
62 | 402 | Pres_Imp_G4 | Presion Impulsion Grupo 4 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | -99.9 | 99.9 | barg | 0.1 | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
63 | 403 | Pres_Ret_G4 | Presion Retorno Grupo 4 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | -99.9 | 99.9 | barg | 0.1 | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
64 | 404 | PDiferG4 | Presion Diferencial Grupo 4 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | -99.9 | 99.9 | barg | 0.1 | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
65 | 405 | Consigna_Presion_G4 | Consigna Presion Grupo 4 | SET_POINT | DEFAULT | simple | 300 | 3 | 6 | 0 | 3276.7 | barg | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
66 | 406 | LecturaPresion_B1_G4 | Presion bomba 1 grupo 4 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 3276.7 | barg | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
67 | 407 | LecturaPresion_B2_G4 | Presion bomba 2 grupo 4 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 3276.7 | barg | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
68 | 408 | LecturaPresion_B3_G4 | Presion bomba 3 grupo 4 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 3276.7 | barg | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
69 | 409 | Frecuencia_conv_10 | Frecuencia actual en Hz | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | Hz | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
70 | 410 | Intensidad_conv_10 | Intensidad actual en A | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | A | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
71 | 411 | Potencia_conv_10 | Potencia actual en KW | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | kw | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
72 | 412 | Frecuencia_conv_11 | Frecuencia actual en Hz | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | Hz | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
73 | 413 | Intensidad_conv_11 | Intensidad actual en A | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | A | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
74 | 414 | Potencia_conv_11 | Potencia actual en KW | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | kw | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
75 | 415 | Frecuencia_conv_12 | Frecuencia actual en Hz | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | Hz | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
76 | 416 | Intensidad_conv_12 | Intensidad actual en A | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | A | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
77 | 417 | Potencia_conv_12 | Potencia actual en KW | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | kw | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
78 | 500 | Temp_Imp_G5 | Temperatura Impulsion Grupo 5 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | -50 | 150 | °C | 0.1 | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
79 | 501 | Temp_Ret_G5 | Temperatura Retorno Grupo 5 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | -50 | 150 | °C | 0.1 | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
80 | 502 | Pres_Imp_G5 | Presion Impulsion Grupo 5 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | -99.9 | 99.9 | barg | 0.1 | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
81 | 503 | Pres_Ret_G5 | Presion Retorno Grupo 5 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | -99.9 | 99.9 | barg | 0.1 | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
82 | 504 | PDiferG5 | Presion Diferencial Grupo 5 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | -99.9 | 99.9 | barg | 0.1 | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
83 | 505 | Consigna_Presion_G5 | Consigna Presion Grupo 5 | SET_POINT | DEFAULT | simple | 300 | 3 | 6 | 0 | 3276.7 | barg | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
84 | 506 | LecturaPresion_B1_G5 | Presion bomba 1 grupo 5 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 3276.7 | barg | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
85 | 507 | LecturaPresion_B2_G5 | Presion bomba 2 grupo 5 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 3276.7 | barg | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
86 | 508 | LecturaPresion_B3_G5 | Presion bomba 3 grupo 5 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 3276.7 | barg | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
87 | 509 | Frecuencia_conv_13 | Frecuencia actual en Hz | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | Hz | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
88 | 510 | Intensidad_conv_13 | Intensidad actual en A | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | A | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
89 | 511 | Potencia_conv_13 | Potencia actual en KW | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | kw | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
90 | 512 | Frecuencia_conv_14 | Frecuencia actual en Hz | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | Hz | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
91 | 513 | Intensidad_conv_14 | Intensidad actual en A | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | A | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
92 | 514 | Potencia_conv_14 | Potencia actual en KW | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | kw | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
93 | 515 | Frecuencia_conv_15 | Frecuencia actual en Hz | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | Hz | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
94 | 516 | Intensidad_conv_15 | Intensidad actual en A | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | A | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
95 | 517 | Potencia_conv_15 | Potencia actual en KW | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | kw | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
96 | 600 | Temp_Imp_G6 | Temperatura Impulsion Grupo 6 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | -50 | 150 | °C | 0.1 | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
97 | 601 | Temp_Ret_G6 | Temperatura Retorno Grupo 6 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | -50 | 150 | °C | 0.1 | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
98 | 602 | Pres_Imp_G6 | Presion Impulsion Grupo 6 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | -99.9 | 99.9 | barg | 0.1 | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
99 | 603 | Pres_Ret_G6 | Presion Retorno Grupo 6 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | -99.9 | 99.9 | barg | 0.1 | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
100 | 604 | PDiferG6 | Presion Diferencial Grupo 6 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | -99.9 | 99.9 | barg | 0.1 | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
101 | 605 | Consigna_Presion_G6 | Consigna Presion Grupo 6 | SET_POINT | DEFAULT | simple | 300 | 3 | 6 | 0 | 3276.7 | barg | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
102 | 606 | LecturaPresion_B1_G6 | Presion bomba 1 grupo 6 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 3276.7 | barg | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
103 | 607 | LecturaPresion_B2_G6 | Presion bomba 2 grupo 6 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 3276.7 | barg | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
104 | 608 | LecturaPresion_B3_G6 | Presion bomba 3 grupo 6 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 3276.7 | barg | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
105 | 609 | Frecuencia_conv_16 | Frecuencia actual en Hz | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | Hz | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
106 | 610 | Intensidad_conv_16 | Intensidad actual en A | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | A | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
107 | 611 | Potencia_conv_16 | Potencia actual en KW | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | kw | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
108 | 612 | Frecuencia_conv_17 | Frecuencia actual en Hz | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | Hz | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
109 | 613 | Intensidad_conv_17 | Intensidad actual en A | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | A | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
110 | 614 | Potencia_conv_17 | Potencia actual en KW | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | kw | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
111 | 615 | Frecuencia_conv_18 | Frecuencia actual en Hz | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | Hz | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
112 | 616 | Intensidad_conv_18 | Intensidad actual en A | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | A | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
113 | 617 | Potencia_conv_18 | Potencia actual en KW | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | kw | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
114 | 700 | Temp_Imp_G7 | Temperatura Impulsion Grupo 5 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | -50 | 150 | °C | 0.1 | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
115 | 701 | Temp_Ret_G7 | Temperatura Retorno Grupo 7 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | -50 | 150 | °C | 0.1 | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
116 | 702 | Pres_Imp_G7 | Presion Impulsion Grupo 7 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | -99.9 | 99.9 | barg | 0.1 | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
117 | 703 | Pres_Ret_G7 | Presion Retorno Grupo 7 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | -99.9 | 99.9 | barg | 0.1 | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
118 | 704 | PDiferG7 | Presion Diferencial Grupo 7 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | -99.9 | 99.9 | barg | 0.1 | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
119 | 705 | Consigna_Presion_G7 | Consigna Presion Grupo 7 | SET_POINT | DEFAULT | simple | 300 | 3 | 6 | 0 | 3276.7 | barg | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
120 | 706 | LecturaPresion_B1_G7 | Presion bomba 1 grupo 7 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 3276.7 | barg | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
121 | 707 | LecturaPresion_B2_G7 | Presion bomba 2 grupo 7 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 3276.7 | barg | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
122 | 708 | LecturaPresion_B3_G7 | Presion bomba 3 grupo 7 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 3276.7 | barg | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
123 | 709 | Frecuencia_conv_19 | Frecuencia actual en Hz | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | Hz | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
124 | 710 | Intensidad_conv_19 | Intensidad actual en A | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | A | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
125 | 711 | Potencia_conv_19 | Potencia actual en KW | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | kw | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
126 | 712 | Frecuencia_conv_20 | Frecuencia actual en Hz | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | Hz | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
127 | 713 | Intensidad_conv_20 | Intensidad actual en A | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | A | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
128 | 714 | Potencia_conv_20 | Potencia actual en KW | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | kw | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
129 | 715 | Frecuencia_conv_21 | Frecuencia actual en Hz | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | Hz | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
130 | 716 | Intensidad_conv_21 | Intensidad actual en A | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | A | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
131 | 717 | Potencia_conv_21 | Potencia actual en KW | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | kw | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
132 | 800 | Temp_Imp_G8 | Temperatura Impulsion Grupo 8 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | -50 | 150 | °C | 0.1 | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
133 | 801 | Temp_Ret_G8 | Temperatura Retorno Grupo 8 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | -50 | 150 | °C | 0.1 | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
134 | 802 | Pres_Imp_G8 | Presion Impulsion Grupo 8 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | -99.9 | 99.9 | barg | 0.1 | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
135 | 803 | Pres_Ret_G8 | Presion Retorno Grupo 8 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | -99.9 | 99.9 | barg | 0.1 | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
136 | 804 | PDiferG8 | Presion Diferencial Grupo 8 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | -99.9 | 99.9 | barg | 0.1 | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
137 | 805 | Consigna_Presion_G8 | Consigna Presion Grupo 8 | SET_POINT | DEFAULT | simple | 300 | 3 | 6 | 0 | 3276.7 | barg | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
138 | 806 | LecturaPresion_B1_G8 | Presion bomba 1 grupo 8 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 3276.7 | barg | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
139 | 807 | LecturaPresion_B2_G8 | Presion bomba 2 grupo 8 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 3276.7 | barg | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
140 | 808 | LecturaPresion_B3_G8 | Presion bomba 3 grupo 8 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 3276.7 | barg | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
141 | 809 | Frecuencia_conv_22 | Frecuencia actual en Hz | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | Hz | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
142 | 810 | Intensidad_conv_22 | Intensidad actual en A | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | A | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
143 | 811 | Potencia_conv_22 | Potencia actual en KW | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | kw | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
144 | 812 | Frecuencia_conv_23 | Frecuencia actual en Hz | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | Hz | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
145 | 813 | Intensidad_conv_23 | Intensidad actual en A | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | A | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
146 | 814 | Potencia_conv_23 | Potencia actual en KW | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | kw | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
147 | 815 | Frecuencia_conv_24 | Frecuencia actual en Hz | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | Hz | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
148 | 816 | Intensidad_conv_24 | Intensidad actual en A | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | A | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
149 | 817 | Potencia_conv_24 | Potencia actual en KW | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | kw | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
150 | 900 | Freq_L_SPV | Frequency | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | Hz | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
151 | 901 | Current_1_L_SPV | Current line 1 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | A | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
152 | 902 | Current_2_L_SPV | Current line 2 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | A | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
153 | 903 | Current_3_L_SPV | Current line 3 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | A | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
154 | 904 | Apparent_Power_1_L_SPV | Reactive power 1 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | kVAr | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
155 | 905 | Apparent_Power_2_L_SPV | Reactive power 2 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | kVAr | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
156 | 906 | Apparent_Power_3_L_SPV | Reactive power 3 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | kVAr | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
157 | 907 | Apparent_Power_L_SPV | Apparent power | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | kVA | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
158 | 908 | Reactive_Power_1_L_SPV | Reactive power 1 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | kVAr | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
159 | 909 | Reactive_Power_2_L_SPV | Reactive power 2 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | kVAr | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
160 | 910 | Reactive_Power_3_L_SPV | Reactive power 3 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | kVAr | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
161 | 911 | Reactive_Power_L_SPV | Reactive power | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | kVAr | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
162 | 912 | Power_1_L_SPV | Power 1 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | kW | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
163 | 913 | Power_2_L_SPV | Power 2 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | kW | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
164 | 914 | Power_3_L_SPV | Power 3 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | kW | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
165 | 915 | Power_L_SPV | Equivalent power | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 | kW | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
166 | 916 | Power_Factor_1_L_SPV | Power factor 1 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 |  | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
167 | 917 | Power_Factor_2_L_SPV | Power factor 2 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 |  | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
168 | 918 | Power_Factor_3_L_SPV | Power factor 3 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 |  | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
169 | 919 | Power_Factor_L_SPV | Power factor | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999.9 |  | 0.1 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
170 | 1 | Unit_Status | Estado General (1:On; 2: Off por alarma; 3: Off por red; 4: | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 13 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
171 | 2 | Msk_Keyboard_OnOff | Temporary variable for manage the OnOff unit status | CONFIG_PARAMETER | DEFAULT | simple | 0 | 1 | 5 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
172 | 3 | Num_Grupos | Numero de Grupos de Bombeo | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 8 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
173 | 4 | DELAY_AL_NO_WATER_FLOW | Delay Alarm No Water Flow | CONFIG_PARAMETER | DEFAULT | simple | 0 | 1 | 5 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
174 | 5 | Max_On_Flow_AL_Time | Maximun Active Alarm Time | CONFIG_PARAMETER | DEFAULT | simple | 0 | 1 | 5 | 1 | 3600 | min | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
175 | 6 | MaxRetry_Flow_Al | maximum number of retries flow alarm | ALARM | DEFAULT | simple | 30 | 1 | 6 | 1 | 9 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
176 | 7 | CheckTime_Flow_AL | Check Time of No Flow Alarm | CONFIG_PARAMETER | DEFAULT | simple | 0 | 1 | 5 | 1 | 3600 | min | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
177 | 8 | Modelo_Variador | Modelo Variador Bomba | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
178 | 100 | Cod_Fallo | Codígo de fallo activo (dir8, fun3) | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 32767 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
179 | 101 | Cod_Fallo_2 | Codígo de fallo activo (dir8, fun3) | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 32767 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
180 | 102 | Cod_Fallo_3 | Codígo de fallo activo (dir8, fun3) | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 32767 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
181 | 103 | Num_Bombas_G1 | Numero de Bombas Grupo 1 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 3 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
182 | 104 | T_H_B1_G1 | Horas totales x1000 bomba 1 grupo 1 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
183 | 105 | T_L_B1_G1 | Horas totales x1 bomba 1 grupo 1 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
184 | 106 | T_H_B2_G1 | Horas totales x1000 bomba 2 grupo 1 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
185 | 107 | T_L_B2_G1 | Horas totales x1 bomba 2 grupo 1 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
186 | 108 | T_H_B3_G1 | Horas totales x1000 bomba 3 grupo 1 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
187 | 109 | T_L_B3_G1 | Horas totales x1 bomba 3 grupo 1 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
188 | 110 | T_ARRAN_32767x10000_B1_G1 | Arranques x10000 bomba 1 grupo 1 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
189 | 111 | T_ARRAN_9999_B1_G1 | Arranques x1 bomba 1 grupo 1 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
190 | 112 | T_ARRAN_32767x10000_B2_G1 | Arranques x10000 bomba 2 grupo 1 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
191 | 113 | T_ARRAN_9999_B2_G1 | Arranques x1 bomba 2 grupo 1 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
192 | 114 | T_ARRAN_32767x10000_B3_G1 | Arranques x10000 bomba 3 grupo 1 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
193 | 115 | T_ARRAN_9999_B3_G1 | Arranques x1 bomba 3 grupo 1 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
194 | 116 | Thr_H_B1_G1 | Máximo horas para mantenimiento bomba 1 grupo 1 | CONFIG_PARAMETER | DEFAULT | simple | 0 | 1 | 5 | 0 | 99 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
195 | 117 | Thr_H_B2_G1 | Máximo horas para mantenimiento bomba 2 grupo 1 | CONFIG_PARAMETER | DEFAULT | simple | 0 | 1 | 5 | 0 | 99 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
196 | 118 | Thr_H_B3_G1 | Máximo horas para mantenimiento bomba 3 grupo 1 | CONFIG_PARAMETER | DEFAULT | simple | 0 | 1 | 5 | 0 | 99 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
197 | 200 | Cod_Fallo_4 | Codígo de fallo activo (dir8, fun3) | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 32767 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
198 | 201 | Cod_Fallo_5 | Codígo de fallo activo (dir8, fun3) | CONFIG_PARAMETER | DEFAULT | simple | 0 | 1 | 5 | 0 | 32767 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
199 | 202 | Cod_Fallo_6 | Codígo de fallo activo (dir8, fun3) | CONFIG_PARAMETER | DEFAULT | simple | 0 | 1 | 5 | 0 | 32767 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
200 | 203 | Num_Bombas_G2 | Numero de Bombas Grupo 2 | CONFIG_PARAMETER | DEFAULT | simple | 0 | 1 | 5 | 0 | 3 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
201 | 204 | T_H_B1_G2 | Horas totales x1000 bomba 1 grupo 2 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
202 | 205 | T_L_B1_G2 | Horas totales x1 bomba 1 grupo 2 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
203 | 206 | T_H_B2_G2 | Horas totales x1000 bomba 2 grupo 2 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
204 | 207 | T_L_B2_G2 | Horas totales x1 bomba 2 grupo 2 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
205 | 208 | T_H_B3_G2 | Horas totales x1000 bomba 3 grupo 2 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
206 | 209 | T_L_B3_G2 | Horas totales x1 bomba 3 grupo 2 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
207 | 210 | T_ARRAN_32767x10000_B1_G2 | Arranques x10000 bomba 1 grupo 2 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
208 | 211 | T_ARRAN_9999_B1_G2 | Arranques x1 bomba 1 grupo 2 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
209 | 212 | T_ARRAN_32767x10000_B2_G2 | Arranques x10000 bomba 2 grupo 2 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
210 | 213 | T_ARRAN_9999_B2_G2 | Arranques x1 bomba 2 grupo 2 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
211 | 214 | T_ARRAN_32767x10000_B3_G2 | Arranques x10000 bomba 3 grupo 2 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
212 | 215 | T_ARRAN_9999_B3_G2 | Arranques x1 bomba 3 grupo 2 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
213 | 216 | Thr_H_B1_G2 | Máximo horas para mantenimiento bomba 1 grupo 2 | CONFIG_PARAMETER | DEFAULT | simple | 0 | 1 | 5 | 0 | 99 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
214 | 217 | Thr_H_B2_G2 | Máximo horas para mantenimiento bomba 2 grupo 2 | CONFIG_PARAMETER | DEFAULT | simple | 0 | 1 | 5 | 0 | 99 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
215 | 218 | Thr_H_B3_G2 | Máximo horas para mantenimiento bomba 3 grupo 2 | CONFIG_PARAMETER | DEFAULT | simple | 0 | 1 | 5 | 0 | 99 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
216 | 300 | Cod_Fallo_7 | Codígo de fallo activo (dir8, fun3) | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 32767 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
217 | 301 | Cod_Fallo_8 | Codígo de fallo activo (dir8, fun3) | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 32767 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
218 | 302 | Cod_Fallo_9 | Codígo de fallo activo (dir8, fun3) | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 32767 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
219 | 303 | Num_Bombas_G3 | Numero de Bombas Grupo 3 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 3 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
220 | 304 | T_H_B1_G3 | Horas totales x1000 bomba 1 grupo 3 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
221 | 305 | T_L_B1_G3 | Horas totales x1 bomba 1 grupo 3 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
222 | 306 | T_H_B2_G3 | Horas totales x1000 bomba 2 grupo 3 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
223 | 307 | T_L_B2_G3 | Horas totales x1 bomba 2 grupo 3 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
224 | 308 | T_H_B3_G3 | Horas totales x1000 bomba 3 grupo 3 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
225 | 309 | T_L_B3_G3 | Horas totales x1 bomba 3 grupo 3 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
226 | 310 | T_ARRAN_32767x10000_B1_G3 | Arranques x10000 bomba 1 grupo 3 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
227 | 311 | T_ARRAN_9999_B1_G3 | Arranques x1 bomba 1 grupo 3 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
228 | 312 | T_ARRAN_32767x10000_B2_G3 | Arranques x10000 bomba 2 grupo 3 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
229 | 313 | T_ARRAN_9999_B2_G3 | Arranques x1 bomba 2 grupo 3 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
230 | 314 | T_ARRAN_32767x10000_B3_G3 | Arranques x10000 bomba 3 grupo 3 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
231 | 315 | T_ARRAN_9999_B3_G3 | Arranques x1 bomba 3 grupo 3 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
232 | 316 | Thr_H_B1_G3 | Máximo horas para mantenimiento bomba 1 grupo 3 | CONFIG_PARAMETER | DEFAULT | simple | 0 | 1 | 5 | 0 | 99 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
233 | 317 | Thr_H_B2_G3 | Máximo horas para mantenimiento bomba 2 grupo 3 | CONFIG_PARAMETER | DEFAULT | simple | 0 | 1 | 5 | 0 | 99 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
234 | 318 | Thr_H_B3_G3 | Máximo horas para mantenimiento bomba 3 grupo 3 | CONFIG_PARAMETER | DEFAULT | simple | 0 | 1 | 5 | 0 | 99 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
235 | 400 | Cod_Fallo_10 | Codígo de fallo activo (dir8, fun3) | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 32767 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
236 | 401 | Cod_Fallo_11 | Codígo de fallo activo (dir8, fun3) | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 32767 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
237 | 402 | Cod_Fallo_12 | Codígo de fallo activo (dir8, fun3) | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 32767 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
238 | 403 | Num_Bombas_G4 | Numero de Bombas Grupo 4 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 3 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
239 | 404 | T_H_B1_G4 | Horas totales x1000 bomba 1 grupo 4 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
240 | 405 | T_L_B1_G4 | Horas totales x1 bomba 1 grupo 4 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
241 | 406 | T_H_B2_G4 | Horas totales x1000 bomba 2 grupo 4 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
242 | 407 | T_L_B2_G4 | Horas totales x1 bomba 2 grupo 4 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
243 | 408 | T_H_B3_G4 | Horas totales x1000 bomba 3 grupo 4 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
244 | 409 | T_L_B3_G4 | Horas totales x1 bomba 3 grupo 4 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
245 | 410 | T_ARRAN_32767x10000_B1_G4 | Arranques x10000 bomba 1 grupo 4 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
246 | 411 | T_ARRAN_9999_B1_G4 | Arranques x1 bomba 1 grupo 4 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
247 | 412 | T_ARRAN_32767x10000_B2_G4 | Arranques x10000 bomba 2 grupo 4 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
248 | 413 | T_ARRAN_9999_B2_G4 | Arranques x1 bomba 2 grupo 4 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
249 | 414 | T_ARRAN_32767x10000_B3_G4 | Arranques x10000 bomba 3 grupo 4 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
250 | 415 | T_ARRAN_9999_B3_G4 | Arranques x1 bomba 3 grupo 4 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
251 | 416 | Thr_H_B1_G4 | Máximo horas para mantenimiento bomba 1 grupo 4 | CONFIG_PARAMETER | DEFAULT | simple | 0 | 1 | 5 | 0 | 99 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
252 | 417 | Thr_H_B2_G4 | Máximo horas para mantenimiento bomba 2 grupo 4 | CONFIG_PARAMETER | DEFAULT | simple | 0 | 1 | 5 | 0 | 99 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
253 | 418 | Thr_H_B3_G4 | Máximo horas para mantenimiento bomba 3 grupo 4 | CONFIG_PARAMETER | DEFAULT | simple | 0 | 1 | 5 | 0 | 99 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
254 | 500 | Cod_Fallo_13 | Codígo de fallo activo (dir8, fun3) | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 32767 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
255 | 501 | Cod_Fallo_14 | Codígo de fallo activo (dir8, fun3) | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 32767 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
256 | 502 | Cod_Fallo_15 | Codígo de fallo activo (dir8, fun3) | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 32767 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
257 | 503 | Num_Bombas_G5 | Numero de Bombas Grupo 5 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 3 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
258 | 504 | T_H_B1_G5 | Horas totales x1000 bomba 1 grupo 5 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
259 | 505 | T_L_B1_G5 | Horas totales x1 bomba 1 grupo 5 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
260 | 506 | T_H_B2_G5 | Horas totales x1000 bomba 2 grupo 5 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
261 | 507 | T_L_B2_G5 | Horas totales x1 bomba 2 grupo 5 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
262 | 508 | T_H_B3_G5 | Horas totales x1000 bomba 3 grupo 5 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
263 | 509 | T_L_B3_G5 | Horas totales x1 bomba 3 grupo 5 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
264 | 510 | T_ARRAN_32767x10000_B1_G5 | Arranques x10000 bomba 1 grupo 5 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
265 | 511 | T_ARRAN_9999_B1_G5 | Arranques x1 bomba 1 grupo 5 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
266 | 512 | T_ARRAN_32767x10000_B3_G5 | Arranques x10000 bomba 3 grupo 5 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
267 | 513 | T_ARRAN_9999_B3_G5 | Arranques x1 bomba 3 grupo 5 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
268 | 514 | T_ARRAN_32767x10000_B2_G5 | Arranques x10000 bomba 2 grupo 5 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
269 | 515 | T_ARRAN_9999_B2_G5 | Arranques x1 bomba 2 grupo 5 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
270 | 516 | Thr_H_B1_G5 | Máximo horas para mantenimiento bomba 1 grupo 5 | CONFIG_PARAMETER | DEFAULT | simple | 0 | 1 | 5 | 0 | 99 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
271 | 517 | Thr_H_B2_G5 | Máximo horas para mantenimiento bomba 2 grupo 5 | CONFIG_PARAMETER | DEFAULT | simple | 0 | 1 | 5 | 0 | 99 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
272 | 518 | Thr_H_B3_G5 | Máximo horas para mantenimiento bomba 3 grupo 5 | CONFIG_PARAMETER | DEFAULT | simple | 0 | 1 | 5 | 0 | 99 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
273 | 600 | Cod_Fallo_16 | Codígo de fallo activo (dir8, fun3) | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 32767 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
274 | 601 | Cod_Fallo_17 | Codígo de fallo activo (dir8, fun3) | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 32767 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
275 | 602 | Cod_Fallo_18 | Codígo de fallo activo (dir8, fun3) | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 32767 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
276 | 603 | Num_Bombas_G6 | Numero de Bombas Grupo 6 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 3 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
277 | 604 | T_H_B1_G6 | Horas totales x1000 bomba 1 grupo 6 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
278 | 605 | T_L_B1_G6 | Horas totales x1 bomba 1 grupo 6 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
279 | 606 | T_H_B2_G6 | Horas totales x1000 bomba 2 grupo 6 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
280 | 607 | T_L_B2_G6 | Horas totales x1 bomba 2 grupo 6 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
281 | 608 | T_H_B3_G6 | Horas totales x1000 bomba 3 grupo 6 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
282 | 609 | T_L_B3_G6 | Horas totales x1 bomba 3 grupo 6 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
283 | 610 | T_ARRAN_32767x10000_B1_G6 | Arranques x10000 bomba 1 grupo 6 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
284 | 611 | T_ARRAN_9999_B1_G6 | Arranques x1 bomba 1 grupo 6 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
285 | 612 | T_ARRAN_32767x10000_B2_G6 | Arranques x10000 bomba 2 grupo 6 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
286 | 613 | T_ARRAN_9999_B2_G6 | Arranques x1 bomba 2 grupo 6 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
287 | 614 | T_ARRAN_32767x10000_B3_G6 | Arranques x10000 bomba 3 grupo 6 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
288 | 615 | T_ARRAN_9999_B3_G6 | Arranques x1 bomba 3 grupo 6 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
289 | 616 | Thr_H_B1_G6 | Máximo horas para mantenimiento bomba 1 grupo 6 | CONFIG_PARAMETER | DEFAULT | simple | 0 | 1 | 5 | 0 | 99 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
290 | 617 | Thr_H_B2_G6 | Máximo horas para mantenimiento bomba 2 grupo 6 | CONFIG_PARAMETER | DEFAULT | simple | 0 | 1 | 5 | 0 | 99 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
291 | 618 | Thr_H_B3_G6 | Máximo horas para mantenimiento bomba 3 grupo 6 | CONFIG_PARAMETER | DEFAULT | simple | 0 | 1 | 5 | 0 | 99 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
292 | 700 | Cod_Fallo_19 | Codígo de fallo activo (dir8, fun3) | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 32767 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
293 | 701 | Cod_Fallo_20 | Codígo de fallo activo (dir8, fun3) | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 32767 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
294 | 702 | Cod_Fallo_21 | Codígo de fallo activo (dir8, fun3) | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 32767 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
295 | 703 | Num_Bombas_G7 | Numero de Bombas Grupo 7 | CONFIG_PARAMETER | DEFAULT | simple | 0 | 1 | 5 | 0 | 3 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
296 | 704 | T_H_B1_G7 | Horas totales x1000 bomba 1 grupo 7 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
297 | 705 | T_L_B1_G7 | Horas totales x1 bomba 1 grupo 7 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
298 | 706 | T_H_B2_G7 | Horas totales x1000 bomba 2 grupo 7 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
299 | 707 | T_L_B2_G7 | Horas totales x1 bomba 2 grupo 7 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
300 | 708 | T_H_B3_G7 | Horas totales x1000 bomba 3 grupo 7 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
301 | 709 | T_L_B3_G7 | Horas totales x1 bomba 3 grupo 7 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
302 | 710 | T_ARRAN_32767x10000_B1_G7 | Arranques x10000 bomba 1 grupo 7 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
303 | 711 | T_ARRAN_9999_B1_G7 | Arranques x1 bomba 1 grupo 7 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
304 | 712 | T_ARRAN_32767x10000_B2_G7 | Arranques x10000 bomba 2 grupo 7 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
305 | 713 | T_ARRAN_9999_B2_G7 | Arranques x1 bomba 2 grupo 7 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
306 | 714 | T_ARRAN_32767x10000_B3_G7 | Arranques x10000 bomba 3 grupo 7 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
307 | 715 | T_ARRAN_9999_B3_G7 | Arranques x1 bomba 3 grupo 7 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
308 | 716 | Thr_H_B1_G7 | Máximo horas para mantenimiento bomba 1 grupo 7 | CONFIG_PARAMETER | DEFAULT | simple | 0 | 1 | 5 | 0 | 99 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
309 | 717 | Thr_H_B2_G7 | Máximo horas para mantenimiento bomba 2 grupo 7 | CONFIG_PARAMETER | DEFAULT | simple | 0 | 1 | 5 | 0 | 99 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
310 | 718 | Thr_H_B3_G7 | Máximo horas para mantenimiento bomba 3 grupo 7 | CONFIG_PARAMETER | DEFAULT | simple | 0 | 1 | 5 | 0 | 99 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
311 | 800 | Cod_Fallo_22 | Codígo de fallo activo (dir8, fun3) | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 32767 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
312 | 801 | Cod_Fallo_23 | Codígo de fallo activo (dir8, fun3) | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 32767 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
313 | 802 | Cod_Fallo_24 | Codígo de fallo activo (dir8, fun3) | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 32767 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
314 | 803 | Num_Bombas_G8 | Numero de Bombas Grupo 8 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 3 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
315 | 804 | T_H_B1_G8 | Horas totales x1000 bomba 1 grupo 8 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
316 | 805 | T_L_B1_G8 | Horas totales x1 bomba 1 grupo 8 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
317 | 806 | T_H_B2_G8 | Horas totales x1000 bomba 2 grupo 8 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
318 | 807 | T_L_B2_G8 | Horas totales x1 bomba 2 grupo 8 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
319 | 808 | T_H_B3_G8 | Horas totales x1000 bomba 3 grupo 8 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
320 | 809 | T_L_B3_G8 | Horas totales x1 bomba 3 grupo 8 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
321 | 810 | T_ARRAN_32767x10000_B1_G8 | Arranques x10000 bomba 1 grupo 8 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
322 | 811 | T_ARRAN_9999_B1_G8 | Arranques x1 bomba 1 grupo 8 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
323 | 812 | T_ARRAN_32767x10000_B2_G8 | Arranques x10000 bomba 2 grupo 8 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
324 | 813 | T_ARRAN_9999_B2_G8 | Arranques x1 bomba 2 grupo 8 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
325 | 814 | T_ARRAN_32767x10000_B3_G8 | Arranques x10000 bomba 3 grupo 8 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
326 | 815 | T_ARRAN_9999_B3_G8 | Arranques x1 bomba 3 grupo 8 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
327 | 816 | Thr_H_B1_G8 | Máximo horas para mantenimiento bomba 1 grupo 8 | CONFIG_PARAMETER | DEFAULT | simple | 0 | 1 | 5 | 0 | 99 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
328 | 817 | Thr_H_B2_G8 | Máximo horas para mantenimiento bomba 2 grupo 8 | CONFIG_PARAMETER | DEFAULT | simple | 0 | 1 | 5 | 0 | 99 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
329 | 818 | Thr_H_B3_G8 | Máximo horas para mantenimiento bomba 3 grupo 8 | CONFIG_PARAMETER | DEFAULT | simple | 0 | 1 | 5 | 0 | 99 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
330 | 900 | Energy_L_MSK | Integer value for mask | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
331 | 901 | Energy_M_MSK | Integer value for mask | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
332 | 902 | Energy_H_MSK | Integer value for mask | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
333 | 903 | Voltage_L1_L2_L_SPV | Voltage L1-L2 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 | V | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
334 | 904 | Voltage_L2_L3_L_SPV | Voltage L2-L3 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 | V | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
335 | 905 | Voltage_L3_L1_L_SPV | Voltage L3-L1 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 | V | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
336 | 906 | Voltage_1_L_SPV | Voltage 1 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 | V | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
337 | 907 | Voltage_2_L_SPV | Voltage 2 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 | V | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
338 | 908 | Voltage_3_L_SPV | Voltage 3 | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 | V | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
339 | 909 | Apparent_Energy_L_MSK | Integer value for mask | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
340 | 910 | Apparent_Energy_M_MSK | Integer value for mask | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
341 | 911 | Apparent_Energy_H_MSK | Integer value for mask | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
342 | 912 | Voltage_L_L_SPV | Voltage V-L | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 32767 | V | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
343 | 913 | Voltage_Average | Phase-phase average voltage | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 32767 | V | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
344 | 914 | Voltage_L_N_SPV | Voltage V-N | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 32767 | V | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
345 | 915 | Power_Factor_1_L_MSK | Integer value for mask | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
346 | 916 | Power_Factor_1_LL_MSK | Integer value for mask | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
347 | 917 | Power_Factor_2_L_MSK | Integer value for mask | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
348 | 918 | Power_Factor_2_LL_MSK | Integer value for mask | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
349 | 919 | Power_Factor_3_L_MSK | Integer value for mask | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
350 | 920 | Power_Factor_3_LL_MSK | Integer value for mask | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
351 | 921 | Power_Factor_L_MSK | Integer value for mask | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
352 | 922 | Power_Factor_LL_MSK | Integer value for mask | DEFAULT | DEFAULT | simple | 0 | 4 | 0 | 0 | 9999 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
353 | 1 | Sys_On | Unidad arrancada | STATUS | DEFAULT | basic | 60 | 4 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
354 | 2 | Din_On_Off | Entrada Marcha/Paro General | STATUS | DEFAULT | basic | 60 | 4 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
355 | 3 | Superv_OnOff | Orden de marcha general desde supervisor | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
356 | 4 | Alarm_Relay | Salida de alarma | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
357 | 5 | AL_COM_GLOBAL | Alarma unidad global | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
358 | 6 | BMS_Res_Alarms | Reset de alarmas desde supervisor | ALARM | DEFAULT | simple | 30 | 1 | 5 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
359 | 7 | Al_Prb_Temp_Imp | Alarma Temperautra Impulsion Desconectada | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
360 | 8 | Al_Prb_Temp_Ret | Alarma Temperautra Retorno Desconectada | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
361 | 9 | Al_Prb_Temp_Imp_2 | Alarma Temperautra Impulsion Desconectada 2 | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
362 | 10 | Al_Prb_Temp_Ret_2 | Alarma Temperautra Retorno Desconectada 2 | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
363 | 11 | Al_Offline_cpCOe_1 | Offline alarm - cpCOe 1 | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
364 | 12 | Al_Offline_cpCOe_2 | Offline alarm - cpCOe 2 | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
365 | 13 | Al_Offline_cpCOe_3 | Offline alarm - cpCOe 3 | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
366 | 14 | Al_Offline_cpCOe_4 | Offline alarm - cpCOe 4 | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
367 | 15 | Al_Offline_cpCOe_5 | Offline alarm - cpCOe 5 | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
368 | 16 | mAl_Clock | Specify if clock board doesn't work or is absent (0: No alar | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
369 | 17 | mAl_Extd_Memory | Specify if P-Memory expansion doesn't work or is absent (0: | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
370 | 100 | Din_On_Off_G1 | Entrada Marcha/Paro Grupo 1 | STATUS | DEFAULT | basic | 60 | 4 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
371 | 101 | OnOff_G1 | Orden de marcha por teclado grupo 1 | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
372 | 102 | EnMarcha_B1_G1 | Bomba 1 grupo 1 en marcha | STATUS | DEFAULT | basic | 60 | 4 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
373 | 103 | EnMarcha_B2_G1 | Bomba 2 grupo 1 en marcha | STATUS | DEFAULT | basic | 60 | 4 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
374 | 104 | EnMarcha_B3_G1 | Bomba 3 grupo 1 en marcha | STATUS | DEFAULT | basic | 60 | 4 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
375 | 105 | Permiso_M_B1_G1_CE | Salida permiso de marcha a bomba 1 grupo 1 por control Exter | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
376 | 107 | Permiso_M_B3_G1_CE | Salida permiso de marcha a bomba 3 grupo 1 control externo | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
377 | 108 | En_T_Imp_Ret_G1 | Enable Supply and Return probe Temperature of Group 1 | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
378 | 109 | Al_Prb_Temp_Imp_G1 | Alarma Temperautra Impulsion Grupo 1 Desconectada | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
379 | 110 | Al_Prb_Temp_Ret_G1 | Alarma Temperautra Retorno Grupo 1 Desconectada | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
380 | 111 | Al_Prb_Pres_Imp_G1 | Alarma Presion Impulsion Desconectada Grupo 1 | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
381 | 112 | Al_Prb_Pres_Ret_G1 | Alarma Presion Retorno Desconectada Grupo 1 | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
382 | 113 | Al_No_Flow_G1 | nan | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
383 | 114 | Alarma_B1_G1 | Alarma bomba 1 grupo 1 | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
384 | 115 | Alarma_B2_G1 | Alarma bomba 2 grupo 1 | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
385 | 116 | Alarma_B3_G1 | Alarma bomba 3 grupo 1 | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
386 | 117 | Al_Offline_B1_G1 | Alarma fuera de linea bomba 1 grupo 1 | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
387 | 118 | Al_Offline_B2_G1 | Alarma fuera de linea bomba 2 grupo 1 | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
388 | 119 | Al_Offline_B3_G1 | Alarma fuera de linea bomba 3 grupo 1 | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
389 | 120 | ResetH_B1_G1 | Puesta a cero contador horas bomba 1 grupo 1 | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
390 | 121 | ResetH_B2_G1 | Puesta a cero contador horas bomba 2 grupo 1 | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
391 | 122 | ResetH_B3_G1 | Puesta a cero contador horas bomba 3 grupo 1 | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
392 | 200 | Din_On_Off_G2 | Entrada Marcha/Paro Grupo 2 | STATUS | DEFAULT | basic | 60 | 4 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
393 | 201 | OnOff_G2 | Orden de marcha por teclado grupo 2 | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
394 | 202 | EnMarcha_B1_G2 | Bomba 1 grupo 2 en marcha | STATUS | DEFAULT | basic | 60 | 4 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
395 | 203 | EnMarcha_B2_G2 | Bomba 2 grupo 2 en marcha | STATUS | DEFAULT | basic | 60 | 4 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
396 | 204 | EnMarcha_B3_G2 | Bomba 3 grupo 2 en marcha | STATUS | DEFAULT | basic | 60 | 4 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
397 | 205 | Permiso_M_B1_G2_CE | Salida permiso de marcha a bomba 1 grupo 2 Control Externo | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
398 | 206 | Permiso_M_B2_G2_CE | Salida permiso de marcha a bomba 2 grupo 2 control externo | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
399 | 207 | Permiso_M_B3_G2_CE | Salida permiso de marcha a bomba 3 grupo 2 control externo | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
400 | 208 | En_T_Imp_Ret_G2 | Enable Supply and Return probe Temperature of Group 2 | STATUS | DEFAULT | basic | 60 | 4 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
401 | 209 | Al_Prb_Temp_Imp_G2 | Alarma Temperautra Impulsion Grupo 2 Desconectada | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
402 | 210 | Al_Prb_Temp_Ret_G2 | Alarma Temperautra Retorno Grupo 2 Desconectada | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
403 | 211 | Al_Prb_Pres_Imp_G2 | Alarma Presion Impulsion Desconectada Grupo 2 | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
404 | 212 | Al_Prb_Pres_Ret_G2 | Alarma Presion Retorno Desconectada Grupo 2 | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
405 | 213 | Al_No_Flow_G2 | nan | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
406 | 214 | Alarma_B1_G2 | Alarma bomba 1 grupo 2 | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
407 | 215 | Alarma_B2_G2 | Alarma bomba 2 grupo 2 | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
408 | 216 | Alarma_B3_G2 | Alarma bomba 3 grupo 2 | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
409 | 217 | Al_Offline_B1_G2 | Alarma fuera de linea bomba 1 grupo 2 | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
410 | 218 | Al_Offline_B2_G2 | Alarma fuera de linea bomba 2 grupo 2 | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
411 | 219 | Al_Offline_B3_G2 | Alarma fuera de linea bomba 3 grupo 2 | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
412 | 220 | ResetH_B1_G2 | Puesta a cero contador horas bomba 1 grupo 2 | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
413 | 221 | ResetH_B2_G2 | Puesta a cero contador horas bomba 2 grupo 2 | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
414 | 222 | ResetH_B3_G2 | Puesta a cero contador horas bomba 3 grupo 2 | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
415 | 300 | Din_On_Off_G3 | Entrada Marcha/Paro Grupo 3 | STATUS | DEFAULT | basic | 60 | 4 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
416 | 301 | OnOff_G3 | Orden de marcha por teclado grupo 3 | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
417 | 302 | EnMarcha_B1_G3 | Bomba 1 grupo 3 en marcha | STATUS | DEFAULT | basic | 60 | 4 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
418 | 303 | EnMarcha_B2_G3 | Bomba 2 grupo 3 en marcha | STATUS | DEFAULT | basic | 60 | 4 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
419 | 304 | EnMarcha_B3_G3 | Bomba 3 grupo 3 en marcha | STATUS | DEFAULT | basic | 60 | 4 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
420 | 305 | Permiso_M_B1_G3_CE | Salida permiso de marcha a bomba 1 grupo 3 control externo | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
421 | 306 | Permiso_M_B2_G3_CE | Salida permiso de marcha a bomba 2 grupo 3 control externo | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
422 | 307 | Permiso_M_B3_G3_CE | Salida permiso de marcha a bomba 3 grupo 3 control externo | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
423 | 308 | En_T_Imp_Ret_G3 | Enable Supply and Return probe Temperature of Group 3 | STATUS | DEFAULT | basic | 60 | 4 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
424 | 309 | Al_Prb_Temp_Imp_G3 | Alarma Temperautra Impulsion Grupo 3 Desconectada | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
425 | 310 | Al_Prb_Temp_Ret_G3 | Alarma Temperautra Retorno Grupo 3 Desconectada | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
426 | 311 | Al_Prb_Pres_Imp_G3 | Alarma Presion Impulsion Desconectada Grupo 3 | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
427 | 312 | Al_Prb_Pres_Ret_G3 | Alarma Presion Retorno Desconectada Grupo 3 | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
428 | 313 | Al_No_Flow_G3 | nan | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
429 | 314 | Alarma_B1_G3 | Alarma bomba 1 grupo 3 | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
430 | 315 | Alarma_B2_G3 | Alarma bomba 2 grupo 3 | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
431 | 316 | Alarma_B3_G3 | Alarma bomba 3 grupo 3 | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
432 | 317 | Al_Offline_B1_G3 | Alarma fuera de linea bomba 1 grupo 3 | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
433 | 318 | Al_Offline_B2_G3 | Alarma fuera de linea bomba 2 grupo 3 | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
434 | 319 | Al_Offline_B3_G3 | Alarma fuera de linea bomba 3 grupo 3 | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
435 | 320 | ResetH_B1_G3 | Puesta a cero contador horas bomba 1 grupo 3 | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
436 | 321 | ResetH_B2_G3 | Puesta a cero contador horas bomba 2 grupo 3 | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
437 | 322 | ResetH_B3_G3 | Puesta a cero contador horas bomba 3 grupo 3 | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
438 | 400 | Din_On_Off_G4 | Entrada Marcha/Paro Grupo 4 | STATUS | DEFAULT | basic | 60 | 4 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
439 | 401 | OnOff_G4 | Orden de marcha por teclado grupo 4 | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
440 | 402 | EnMarcha_B1_G4 | Bomba 1 grupo 4 en marcha | STATUS | DEFAULT | basic | 60 | 4 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
441 | 403 | EnMarcha_B2_G4 | Bomba 2 grupo 4 en marcha | STATUS | DEFAULT | basic | 60 | 4 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
442 | 404 | EnMarcha_B3_G4 | Bomba 3 grupo 4 en marcha | STATUS | DEFAULT | basic | 60 | 4 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
443 | 405 | Permiso_M_B1_G4_CE | Salida permiso de marcha a bomba 1 grupo 4 control externo | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
444 | 406 | Permiso_M_B2_G1_CE | Salida permiso de marcha a bomba 2 grupo 1 por control exter | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
445 | 407 | Permiso_M_B3_G4_CE | Salida permiso de marcha a bomba 3 grupo 4 control externo | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
446 | 408 | En_T_Imp_Ret_G4 | Enable Supply and Return probe Temperature of Group 4 | STATUS | DEFAULT | basic | 60 | 4 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
447 | 409 | Al_Prb_Temp_Imp_G4 | Alarma Temperautra Impulsion Grupo 4 Desconectada | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
448 | 410 | Al_Prb_Temp_Ret_G4 | Alarma Temperautra Retorno Grupo 4 Desconectada | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
449 | 411 | Al_Prb_Pres_Imp_G4 | Alarma Presion Impulsion Desconectada Grupo 4 | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
450 | 412 | Al_Prb_Pres_Ret_G4 | Alarma Presion Retorno Desconectada Grupo 4 | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
451 | 413 | Al_No_Flow_G4 | nan | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
452 | 414 | Alarma_B1_G4 | Alarma bomba 1 grupo 4 | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
453 | 415 | Alarma_B2_G4 | Alarma bomba 2 grupo 4 | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
454 | 416 | Alarma_B3_G4 | Alarma bomba 3 grupo 4 | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
455 | 417 | Al_Offline_B1_G4 | Alarma fuera de linea bomba 1 grupo 4 | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
456 | 418 | Al_Offline_B2_G4 | Alarma fuera de linea bomba 2 grupo 4 | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
457 | 419 | Al_Offline_B3_G4 | Alarma fuera de linea bomba 3 grupo 4 | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
458 | 420 | ResetH_B1_G4 | Puesta a cero contador horas bomba 1 grupo 4 | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
459 | 421 | ResetH_B2_G4 | Puesta a cero contador horas bomba 2 grupo 4 | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
460 | 422 | ResetH_B3_G4 | Puesta a cero contador horas bomba 3 grupo 4 | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
461 | 500 | Din_On_Off_G5 | Entrada Marcha/Paro Grupo 5 | STATUS | DEFAULT | basic | 60 | 4 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
462 | 501 | OnOff_G5 | Orden de marcha por teclado grupo 5 | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
463 | 502 | EnMarcha_B1_G5 | Bomba 1 grupo 5 en marcha | STATUS | DEFAULT | basic | 60 | 4 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
464 | 503 | EnMarcha_B2_G5 | Bomba 2 grupo 5 en marcha | STATUS | DEFAULT | basic | 60 | 4 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
465 | 504 | EnMarcha_B3_G5 | Bomba 3 grupo 5 en marcha | STATUS | DEFAULT | basic | 60 | 4 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
466 | 505 | Permiso_M_B1_G5_CE | Salida permiso de marcha a bomba 1 grupo 5 control externo | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
467 | 506 | Permiso_M_B2_G5_CE | Salida permiso de marcha a bomba 2 grupo 5 control externo | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
468 | 507 | Permiso_M_B3_G5_CE | Salida permiso de marcha a bomba 3 grupo 5 control externo | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
469 | 508 | En_T_Imp_Ret_G5 | Habilitar sondas de temperatura impulsion y retorno grupo 5 | STATUS | DEFAULT | basic | 60 | 4 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
470 | 509 | Al_Prb_Temp_Imp_G5 | Alarma Temperautra Impulsion Grupo 5 Desconectada | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
471 | 510 | Al_Prb_Temp_Ret_G5 | Alarma Temperautra Retorno Grupo 5 Desconectada | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
472 | 511 | Al_Prb_Pres_Imp_G5 | Alarma Presion Impulsion Desconectada Grupo 5 | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
473 | 512 | Al_Prb_Pres_Ret_G5 | Alarma Presion Retorno Desconectada Grupo 5 | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
474 | 513 | Al_No_Flow_G5 | nan | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
475 | 514 | Alarma_B1_G5 | Alarma bomba 1 grupo 5 | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
476 | 515 | Alarma_B2_G5 | Alarma bomba 2 grupo 5 | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
477 | 516 | Alarma_B3_G5 | Alarma bomba 3 grupo 5 | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
478 | 517 | Al_Offline_B1_G5 | Alarma fuera de linea bomba 1 grupo 5 | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
479 | 518 | Al_Offline_B2_G5 | Alarma fuera de linea bomba 2 grupo 5 | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
480 | 519 | Al_Offline_B3_G5 | Alarma fuera de linea bomba 3 grupo 5 | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
481 | 520 | ResetH_B1_G5 | Puesta a cero contador horas bomba 1 grupo 5 | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
482 | 521 | ResetH_B2_G5 | Puesta a cero contador horas bomba 2 grupo 5 | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
483 | 522 | ResetH_B3_G5 | Puesta a cero contador horas bomba 3 grupo 5 | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
484 | 600 | Din_On_Off_G6 | Entrada Marcha/Paro Grupo 6 | STATUS | DEFAULT | basic | 60 | 4 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
485 | 601 | OnOff_G6 | Orden de marcha por teclado grupo 6 | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
486 | 602 | EnMarcha_B1_G6 | Bomba 1 grupo 6 en marcha | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
487 | 603 | EnMarcha_B2_G6 | Bomba 2 grupo 6 en marcha | STATUS | DEFAULT | basic | 60 | 4 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
488 | 604 | EnMarcha_B3_G6 | Bomba 3 grupo 6 en marcha | STATUS | DEFAULT | basic | 60 | 4 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
489 | 605 | Permiso_M_B1_G6_CE | Salida permiso de marcha a bomba 1 grupo 6 control externo | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
490 | 606 | Permiso_M_B2_G6_CE | Salida permiso de marcha a bomba 2 grupo 6 control externo | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
491 | 607 | Permiso_M_B3_G6_CE | Salida permiso de marcha a bomba 3 grupo 6 control externo | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
492 | 608 | En_T_Imp_Ret_G6 | Enable Supply and Return probe Temperature of Group 6 | STATUS | DEFAULT | basic | 60 | 4 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
493 | 609 | Al_Prb_Temp_Imp_G6 | Alarma Temperautra Impulsion Grupo 6 Desconectada | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
494 | 610 | Al_Prb_Temp_Ret_G6 | Alarma Temperautra Retorno Grupo 6 Desconectada | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
495 | 611 | Al_Prb_Pres_Imp_G6 | Alarma Presion Impulsion Desconectada Grupo 6 | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
496 | 612 | Al_Prb_Pres_Ret_G6 | Alarma Presion Retorno Desconectada Grupo 6 | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
497 | 613 | Al_No_Flow_G6 | nan | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
498 | 614 | Alarma_B1_G6 | Alarma bomba 1 grupo 6 | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
499 | 615 | Alarma_B2_G6 | Alarma bomba 2 grupo 6 | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
500 | 616 | Alarma_B3_G6 | Alarma bomba 3 grupo 6 | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
501 | 617 | Al_Offline_B1_G6 | Alarma fuera de linea bomba 1 grupo 6 | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
502 | 618 | Al_Offline_B2_G6 | Alarma fuera de linea bomba 2 grupo 6 | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
503 | 619 | Al_Offline_B3_G6 | Alarma fuera de linea bomba 3 grupo 6 | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
504 | 620 | ResetH_B1_G6 | Puesta a cero contador horas bomba 1 grupo 6 | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
505 | 621 | ResetH_B2_G6 | Puesta a cero contador horas bomba 2 grupo 6 | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
506 | 622 | ResetH_B3_G6 | Puesta a cero contador horas bomba 3 grupo 6 | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
507 | 700 | Din_On_Off_G7 | Entrada Marcha/Paro Grupo 7 | STATUS | DEFAULT | basic | 60 | 4 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
508 | 701 | OnOff_G7 | Orden de marcha por teclado grupo 7 | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
509 | 702 | EnMarcha_B1_G7 | Bomba 1 grupo 7 en marcha | STATUS | DEFAULT | basic | 60 | 4 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
510 | 703 | EnMarcha_B2_G7 | Bomba 2 grupo 7 en marcha | STATUS | DEFAULT | basic | 60 | 4 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
511 | 704 | EnMarcha_B3_G7 | Bomba 3 grupo 7 en marcha | STATUS | DEFAULT | basic | 60 | 4 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
512 | 705 | Permiso_M_B1_G7_CE | Salida permiso de marcha a bomba 1 grupo 7 control externo | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
513 | 706 | Permiso_M_B2_G7_CE | Salida permiso de marcha a bomba 2 grupo 7 control externo | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
514 | 707 | Permiso_M_B3_G7_CE | Salida permiso de marcha a bomba 3 grupo 7 control externo | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
515 | 708 | En_T_Imp_Ret_G7 | Enable Supply and Return probe Temperature of Group 7 | STATUS | DEFAULT | basic | 60 | 4 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
516 | 709 | Al_Prb_Temp_Imp_G7 | Alarma Temperautra Impulsion Grupo 7 Desconectada | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
517 | 710 | Al_Prb_Temp_Ret_G7 | Alarma Temperautra Retorno Grupo 7 Desconectada | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
518 | 711 | Al_Prb_Pres_Imp_G7 | Alarma Presion Impulsion Desconectada Grupo 7 | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
519 | 712 | Al_Prb_Pres_Ret_G7 | Alarma Presion Retorno Desconectada Grupo 7 | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
520 | 713 | Al_No_Flow_G7 | nan | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
521 | 714 | Alarma_B1_G7 | Alarma bomba 1 grupo 7 | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
522 | 715 | Alarma_B2_G7 | Alarma bomba 2 grupo 7 | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
523 | 716 | Alarma_B3_G7 | Alarma bomba 3 grupo 7 | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
524 | 717 | Al_Offline_B1_G7 | Alarma fuera de linea bomba 1 grupo 7 | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
525 | 718 | Al_Offline_B2_G7 | Alarma fuera de linea bomba 2 grupo 7 | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
526 | 719 | Al_Offline_B3_G7 | Alarma fuera de linea bomba 3 grupo 7 | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
527 | 720 | ResetH_B1_G7 | Puesta a cero contador horas bomba 1 grupo 7 | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
528 | 721 | ResetH_B2_G7 | Puesta a cero contador horas bomba 2 grupo 7 | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
529 | 722 | ResetH_B3_G7 | Puesta a cero contador horas bomba 3 grupo 7 | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
530 | 800 | Din_On_Off_G8 | Entrada Marcha/Paro Grupo 8 | STATUS | DEFAULT | basic | 60 | 4 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
531 | 801 | OnOff_G8 | Orden de marcha por teclado grupo 8 | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
532 | 802 | EnMarcha_B1_G8 | Bomba 1 grupo 8 en marcha | STATUS | DEFAULT | basic | 60 | 4 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
533 | 803 | EnMarcha_B2_G8 | Bomba 2 grupo 8 en marcha | STATUS | DEFAULT | basic | 60 | 4 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
534 | 804 | EnMarcha_B3_G8 | Bomba 3 grupo 8 en marcha | STATUS | DEFAULT | basic | 60 | 4 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
535 | 805 | Permiso_M_B1_G8_CE | Salida permiso de marcha a bomba 1 grupo 8 control externo | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
536 | 806 | Permiso_M_B2_G8_CE | Salida permiso de marcha a bomba 2 grupo 8 control externo | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
537 | 807 | Permiso_M_B3_G8_CE | Salida permiso de marcha a bomba 3 grupo 8 control externo | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
538 | 808 | En_T_Imp_Ret_G8 | Enable Supply and Return probe Temperature of Group 8 | STATUS | DEFAULT | basic | 60 | 4 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
539 | 809 | Al_Prb_Temp_Imp_G8 | Alarma Temperautra Impulsion Grupo 8 Desconectada | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
540 | 810 | Al_Prb_Temp_Ret_G8 | Alarma Temperautra Retorno Grupo 8 Desconectada | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
541 | 811 | Al_Prb_Pres_Imp_G8 | Alarma Presion Impulsion Desconectada Grupo 8 | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
542 | 812 | Al_Prb_Pres_Ret_G8 | Alarma Presion Retorno Desconectada Grupo 8 | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
543 | 813 | Al_No_Flow_G8 | nan | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
544 | 814 | Alarma_B1_G8 | Alarma bomba 1 grupo 8 | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
545 | 815 | Alarma_B2_G8 | Alarma bomba 2 grupo 8 | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
546 | 816 | Alarma_B3_G8 | Alarma bomba 3 grupo 8 | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
547 | 817 | Al_Offline_B1_G8 | Alarma fuera de linea bomba 1 grupo 8 | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
548 | 818 | Al_Offline_B2_G8 | Alarma fuera de linea bomba 2 grupo 8 | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
549 | 819 | Al_Offline_B3_G8 | Alarma fuera de linea bomba 3 grupo 8 | ALARM | DEFAULT | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
550 | 820 | ResetH_B1_G8 | Puesta a cero contador horas bomba 1 grupo 8 | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
551 | 821 | ResetH_B2_G8 | Puesta a cero contador horas bomba 2 grupo 8 | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
552 | 822 | ResetH_B3_G8 | Puesta a cero contador horas bomba 3 grupo 8 | COMMAND | DEFAULT | simple | 0 | 0 | 6 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
553 | 900 | Al_Offline_medidor_energia | Alarma fuera de linea medidor energia | ALARM | ALARMS | simple | 30 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus
554 | 901 | HAB_MEDIDOR | Habilitar medidor energía | STATUS | DEFAULT | basic | 60 | 4 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"en_US","translations":{"en_US":{"name":null,"_type":"languages","description":null}}} | [] | modbus