## Hoja1
address allocation table
address |  | content | defalut value | STEP | scope | state | unit
Dashboard status:
Parameters that can only be read cannot be changed or set
Temperature value of the slave machine board:
01~20 : Actual value = register value /10 , that is, data with one decimal place. 21~24: Actual value = register value /4
1 |  | Ambient temperature (signed char) | 0 | - | -30~125 | R | ℃
2 |  | Inlet water temperature (signed char) | 0 | - | -30~125 | R | ℃
3 |  | Return water temperature (signed char) | 0 | - | -30~125 | R | ℃
4 |  | Water tank 1 temperature (signed char) | 0 | - | -30~125 | R | ℃
5 |  | Coil 1 temperature (signed char) | 0 | - | -30~125 | R | ℃
6 |  | Coil 2 temperature (signed char) | 0 | - | -30~125 | R | ℃
7 |  | Suction 1 temperature (signed char) | 0 | - | -30~125 | R | ℃
8 |  | Suction 2 Temperature (signed char) | 0 | - | -30~125 | R | ℃
9 |  | Exhaust 1 temperature | 0 | - | 20~135 | R | ℃
10 |  | Exhaust 2 temperature | 0 | - | 20~135 | R | ℃
11 |  | Cooling inlet 1 temperature | 0 | - | -30~125 | R | ℃
12 |  | Cooling inlet 2 temperature | 0 | - | -30~125 | R | ℃
13 |  | Intercooling inlet temperature 1 | 0 | - | -30~125 | R | ℃
14 |  | Intercooling inlet temperature 2 | 0 | - | -30~125 | R | ℃
15 |  | Intercooling outlet temperature 1 | 0 | - | -30~125 | R | ℃
16 |  | Intercooling outlet temperature 2 | 0 | - | -30~125 | R | ℃
17 |  | (Not used as reserved) | 0 | - | 0~255 | R | ℃
18 |  | (Not used as reserved) | 0 | - | 0~255 | R | ℃
19 |  | Compressor 1 current | 0 | 1 | 0~255 | R | -
20 |  | Compressor 2 current | 0 | 1 | 0~255 | R | -
21 |  | Electronic expansion valve opening 1 main circuit | 0 | 1 | 0~255 | R | -
22 |  | Electronic expansion valve opening 2 main circuit | 0 | 1 | 0~255 | R | -
23 |  | Electronic expansion valve opening 1 auxiliary circuit | 0 | 1 | 0~255 | R | -
24 |  | Electronic expansion valve opening 2 auxiliary circuit | 0 | 1 | 0~255 | R | -
address allocation table
address |  | content | content | default value | STEP | scope | unit
25 |  |  | reserved | 0 | 1 | 0~255 | -
The status of the slave machine board:
26 | B 0 | Ambient temperature status (0 normal, 1 fault) | 0 | - | 0~1 | R | -
| B1 | Inlet water temperature status (0 normal, 1 fault) | 0 | - | 0~1 | R | -
| B2 | Return water temperature status (0 normal, 1 fault) | 0 | - | 0~1 | R | -
| B3 | Water tank 1 temperature status (0 normal, 1 fault) | 0 | - | 0~1 | R | -
| B4 | Coil 1 temperature status (0 normal, 1 fault) | 0 | - | 0~1 | R | -
| B5 | Coil 2 temperature status (0 normal, 1 fault) | 0 | - | 0~1 | R | -
| B6 | Suction 1 temperature status (0 normal, 1 fault) | 0 | - | 0~1 | R | -
| B7 | Suction 2 temperature status (0 normal, 1 fault) | 0 | - | 0~1 | R | -
27 H2 | B0 | Exhaust 1 temperature status (0 normal, 1 fault) | 0 | - | 0~1 | R | -
| B1 | Exhaust 2 temperature status (0 normal, 1 fault) | 0 | - | 0~1 | R | -
| B2 | Cooling inlet 1 temperature state (0 normal, 1 fault) | 0 | - | 0~1 | R | -
| B3 | Cooling inlet 2 temperature states (0 normal, 1 fault) | 0 | - | 0~1 | R | -
| B4 | Intercooling inlet temperature 1 status (0 normal, 1 fault) | 0 | - | 0~1 | R | -
| B5 | Intercooling inlet temperature 2 status (0 normal, 1 fault) | 0 | - | 0~1 | R | -
| B6 | Intercooler outlet temperature 1 status (0 normal, 1 fault) | 0 | - | 0~1 | R | -
| B7 | Intercooler outlet temperature 2 status (0 normal, 1 fault) | 0 | - | 0~1 | R | -
28 H3 | B0 | Outlet water temperature is too high fault (0 normal, normal, 1 fault) | 0 | - | 0~1 | R | -
| B1 | Outlet water temperature is too low fault (0 normal, 1 fault) | 0 | - | 0~1 | R | -
| B2 | Reserved (0 normal, 1 fault) | 0 | - | 0~1 | R | -
| B3 | Reserved (0 normal, 1 fault) | 0 | - | 0~1 | R | -
| B4 | Reserved (0 normal, 1 fault) | 0 | - | 0~1 | R | -
address allocation table
default
address |  |  | content | value | STEP | scope | state | unit
|  | B5 | Undervoltage and overvoltage fault (0 | 0 | - | 0~1 | R | -
normal, 1 fault)
|  | B6 | Cooling inlet 1 low temperature state (0 | 0 | - | 0~1 | R | -
normal, 1 fault)
|  | B7 | Cooling inlet 2 low temperature status (0 | 0 | - | 0~1 | R | -
normal, 1 fault)
|  | B 0 | Low pressure switch 1 (0 normal, 1 fault) | 0 | - | 0~1 | R | -
|  | B1 | Low pressure switch 2 (0 normal, 1 fault) | 0 | - | 0~1 | R | -
|  | B2 | Low pressure switch 3 (0 normal, 1 fault) | 0 | - | 0~1 | R | -
|  | B3 | Low pressure switch 4 (0 normal, 1 fault) | 0 | - | 0~1 | R | -
29 |  | B4 | High pressure switch 1 (0 normal, 1 fault) | 0 | - | 0~1 | R | -
H4 |  | B5 | High pressure switch 2 (0 normal, 1 fault) | 0 | - | 0~1 | R | -
|  | B6 | High pressure switch 3 (0 normal, 1 fault) | 0 | - | 0~1 | R | -
|  | B7 | High pressure switch 4 (0 normal, 1 fault) | 0 | - | 0~1 | R | -
|  | B 0 | Overcurrent switch 1 (0 normal, 1 fault) | 0 | - | 0~1 | R | -
|  | B1 | Overcurrent switch 2 (0 normal, 1 fault) | 0 | - | 0~1 | R | -
|  | B2 | Overcurrent switch 3 (0 normal, 1 fault) | 0 | - | 0~1 | R | -
|  | B3 | Overcurrent switch 4 (0 normal, 1 fault) | 0 | - | 0~1 | R | -
|  | B4 | Exhaust protection 1 (0 normal, 1 fault) | 0 | - | 0~1 | R | -
30 |  | B5 | Exhaust protection 2 (0 normal, 1 fault) | 0 | - | 0~1 | R | -
H5 |  | B6 | Exhaust protection 3 (0 normal, 1 fault) | 0 | - | 0~1 | R | -
|  | B7 | Exhaust protection 4 (0 normal, 1 fault) | 0 | - | 0~1 | R | -
|  | B 0 | The temperature difference between water | 0 | - | 0~1 | R | -
inlet and outlet is too high (0 normal, 1 fault)
|  | B1 | Phase loss or reverse phase (0 normal, 1 | 0 | - | 0~1 | R | -
fault)
|  | B2 | Water flow switch (0 normal, 1 fault) | 0 | - | 0~1 | R | -
31 |  | B3 | Water pressure switch (0 normal, 1 fault) | 0 | - | 0~1 | R | -
H6 |  | B4 | Low water level switch (0 normal, 1 fault) | 0 | - | 0~1 | R | -
|  | B5 | High water level switch (0 normal, 1 fault) | 0 | - | 0~1 | R | -
|  | B6 | Outlet water temperature is too low (0 | 0 | - | 0~1 | R | -
normal, 1 fault)
|  | B7 | (Not used as reserved) | 0 | - | 0~1 | R | -
|  | B 0 | (Not used as reserved) | 0 | - | 0~1 | R | -
32 |  | B1 | (Not used as reserved) | 0 | - | 0~1 | R | -
H7 |  | B2 | (Not used as reserved) | 0 | - | 0~1 | R | -
|  | B3 | (Not used as reserved) | 0 | - | 0~1 | R | -
address allocation table
default
address |  |  | content | value | STEP | scope | state | unit
|  | B4 | (Not used as reserved) | 0 | - | 0~1 | R | -
|  | B5 | (Not used as reserved) | 0 | - | 0~1 | R | -
|  | B6 | (Not used as reserved) | 0 | - | 0~1 | R | -
|  | B 7 | (Not used as reserved) | 0 | - | 0~1 | R | -
|  | B 0 | (Not used as reserved) | 0 | - | 0~1 | R | -
|  | B1 | (Not used as reserved) | 0 | - | 0~1 | R | -
|  | B2 | (Not used as reserved) | 0 | - | 0~1 | R | -
|  | B3 | (Not used as reserved) | 0 | - | 0~1 | R | -
33 |  | B4 | (Not used as reserved) | 0 | - | 0~1 | R | -
H8 |  | B5 | (Not used as reserved) | 0 | - | 0~1 | R | -
|  | B6 | (Not used as reserved) | 0 | - | 0~1 | R | -
|  | B 7 | (Not used as reserved) | 0 | - | 0~1 | R | -
|  | B0 | Linkage switch (0 normal, 1 fault) | 0 | - | 0~1 | R | -
|  | B1 | Reverse phase status (0 normal, 1 fault) | 0 | - | 0~1 | R | -
|  | B2 | Phase loss B status (0 normal, 1 fault) | 0 | - | 0~1 | R | -
|  | B3 | Phase loss C status (0 normal, 1 fault) | 0 | - | 0~1 | R | -
|  | B4 | There is a fault lock that needs to alarm (0 | 0 | - | 0~1 | R | -
normal, 1 fault)
34 |  | B5 | (Not used as reserved) | 0 | - | 0~1 | R | -
H9 |  | B6 | (Not used as reserved) | 0 | - | 0~1 | R | -
|  | B7 | (Not used as reserved) | 0 | - | 0~1 | R | -
|  | B 0 | The quality of EE24C02 (0 normal, 1 fault) | 0 | - | 0~1 | R | -
|  | B1 | Defrost (0 is not present, 1 is present) | 0 | - | 0~1 | R | -
|  | B2 | Antifreeze (0 is not present, 1 is present) | 0 | - | 0~1 | R | -
|  | B3 | Communication status (0 normal, 1 fault) | 0 | - | 0~1 | R | -
35 |  | B4 | (Not used as reserved) | 0 | - | 0~1 | R | -
H10 |  | B5 | (Not used as reserved) | 0 | - | 0~1 | R | -
|  | B6 | (Not used as reserved) | 0 | - | 0~1 | R | -
|  | B7 | (Not used as reserved) | 0 | - | 0~1 | R | -
|  | B 0 | Compressor 1 (0 off, 1 on) | 0 | - | 0~1 | R | -
|  | B1 | Compressor 2 (0 off, 1 on) | 0 | - | 0~1 | R | -
36 |  | B2 | Compressor 3 (0 off, 1 on) | 0 | - | 0~1 | R | -
R1 |  | B3 | Compressor 4 (0 off, 1 on) | 0 | - | 0~1 | R | -
|  | B4 | 4-way valve 1 (0 closes, 1 opens) | 0 | - | 0~1 | R | -
|  | B5 | Fan high speed (0 off, 1 on) | 0 | - | 0~1 | R | -
address allocation table
default
address |  |  | content | value | STEP | scope | state | unit
|  | B6 | Fan low speed(0 off, 1 on) | 0 | - | 0~1 | R | -
|  | B7 | Circulation pump (0 off, 1 on) | 0 | - | 0~1 | R | -
|  | B 0 | Water pump (0 off, 1 on) | 0 | - | 0~1 | R | -
|  | B1 | Water return valve (0 closes, 1 opens) | 0 | - | 0~1 | R | -
|  | B2 | Auxiliary electric heater power (0 turns off, 1 | 0 | - | 0~1 | R | -
turns on)
37 |  | B3 | Alarm (0 off, 1 on) | 0 | - | 0~1 | R | -
R2 |  | B4 | Spray valve 1 (0 closes, 1 opens) | 0 | - | 0~1 | R | -
|  | B5 | Spray valve 2 (0 closes, 1 opens) | 0 | - | 0~1 | R | -
|  | B6 | Spray valve 3 (0 closes, 1 opens) | 0 | - | 0~1 | R | -
|  | B7 | Spray valve 4 (0 closes, 1 opens) | 0 | - | 0~1 | R | -
|  | B 0 | (Not used as reserved) | 0 | - | 0~1 | R | -
|  | B1 | (Not used as reserved) | 0 | - | 0~1 | R | -
|  | B2 | (Not used as reserved) | 0 | - | 0~1 | R | -
|  | B3 | (Not used as reserved) | 0 | - | 0~1 | R | -
38 |  | B4 | (Not used as reserved) | 0 | - | 0~1 | R | -
R3 |  | B5 | (Not used as reserved) | 0 | - | 0~1 | R | -
|  | B6 | (Not used as reserved) | 0 | - | 0~1 | R | -
|  | B7 | (Not used as reserved) | 0 | - | 0~1 | R | -
Parameters that can be read and written: Command code: (Send command to slave) The range of parameters is subject to each specification.
39 |  |  | Heating set temperature | Variety | 1 | 5~60 | R/W | -
40 |  |  | command reservation | 0 | 1 | 0~255 | R/W
41 |  |  | System operating mode (0 cooling, 1 heating) | 0 | 1 | 0~255 | R/W
42 |  |  | command reservation | 0 | 1 | 0~255 | R/W
43 |  |  | Cooling set temperature | 0 | 1 | 10~35 | R/W
44 |  |  | command reservation | 0 | 1 | 0~255 | R/W
|  | B 0 | Power on/off command (0 to turn off, 1 to | 0 | - | 0~1 | R/W | -
turn on)
|  | B1 | Manual electric heating command (0 off, 1 | 0 | - | 0~1 | R/W | -
on)
45 |  | B2 | command reservation | 0 | - | 0~1 | R/W | -
|  | B3 | command reservation | 0 | - | 0~1 | R/W | -
|  | B4 | command reservation | 0 | - | 0~1 | R/W | -
|  | B5 | command reservation | 0 | - | 0~1 | R/W | -
|  | B6 | command reservation | 0 | - | 0~1 | R/W | -
address allocation table
default
address |  |  | content | value | STEP | scope | state | unit
|  | B7 | command reservation | 0 | - | 0~1 | R/W | -
|  | B 0 | command reservation | 0 | - | 0~1 | R/W | -
|  | B1 | command reservation | 0 | - | 0~1 | R/W | -
|  | B2 | command reservation | 0 | - | 0~1 | R/W | -
|  | B3 | command reservation | 0 | - | 0~1 | R/W | -
46 |  | B4 | command reservation | 0 | - | 0~1 | R/W | -
|  | B5 | command reservation | 0 | - | 0~1 | R/W | -
|  | B6 | command reservation | 0 | - | 0~1 | R/W | -
|  | B7 | command reservation | 0 | - | 0~1 | R/W | -
The following are commands that need to be sent to a slave individually:
|  | B 0 | command reservation | 0 | - | 0~1 | R/W | -
|  | B1 | Forced defrost command (0 off, 1 on) | 0 | - | 0~1 | R/W | -
|  | B2 | command reservation | 0 | - | 0~1 | R/W | -
|  | B3 | command reservation | 0 | - | 0~1 | R/W | -
|  | B4 | command reservation | 0 | - | 0~1 | R/W | -
47 |  | B5 | command reservation | 0 | - | 0~1 | R/W | -
|  | B6 | command reservation | 0 | - | 0~1 | R/W | -
|  | B7 | command reservation | 0 | - | 0~1 | R/W | -
48 |  |  | command reservation | 0 | 1 | 0~255 | R/W
Parameter setting items:
49 |  |  | C1_compressor start and stop temperature | 5 | 1 | 2~ 20 | R/W | ℃
difference
50 |  |  | C2_Energy level detection cycle | 0 | 1 | 0 ~50 | R/W | ℃
51 |  |  | C3_ Outlet water temperature is too high | 55 | 1 | 50 ~ 80 | R/W | ℃
|  |  | protection |  |  | _
52 |  |  | C4_ Outlet water temperature is too low | 4 | 1 | 2~10 | R/W | ℃
protection
53 |  |  | C5_Inlet and outlet water temperature | 10 | 1 | 5~ 50 | R/W | ℃
difference protection
54 |  |  | C6_Inlet water temperature correction | 0 | 1 | -9~9 | R/W | ℃
55 |  |  | C7_ambient temperature for auxiliary | 4 | 1 | - 3 0~ 5 | R/W | ℃
|  |  | electric heater automatically start |  |  | 0
56 |  |  | C8_enthalpy increasing input temperature | 10 | 1 | -30~50 | R/W | ℃
57 |  |  | C9_enthalpy increase input temperature | 2 | 1 | 1~10 | R/W | ℃
difference
58 |  |  | CA_Ambient temperature for fan speed | 28 | 1 | 10～40 | R/W | ℃
switching
address allocation table
default
address |  | content | value | STEP | scope | state | unit
59 |  | CB_ambient temperature for heating tape | 2 | 1 | -30～10 | R/W | ℃
start (defrost electric heating)
60 |  | CC_Heating tape running time (defrost | 10 | 1 | 0～60 | R/W | MIN
electric heating)
61 |  | CD_exhaust protection temperature value | 120 | 1 | 90～140 | R/W | ℃
62 |  | CE_ambient temperature set value | 25 | 1 | 10~35 | R/W | ℃
63 |  | CF_ambient temperature difference | 3 | 1 | 2~10 | R/W | ℃
64 |  | A1_Water pump installation method (0: both | 0 | 1 | 0~2 | R/W | -
master and slave have, 1: only master have)
65 |  | A2_Water pump operating mode (0: standby off 1: standby not off) | 1 | 1 | 0~2 | R/W | -
66 |  | A3_Refrigerant collection mode (0 invalid, 1 | 0 | 1 | 0~2 | R/W | -
valid)
67 |  | A4_auxiliary electric heater control mode (0 | 0 | 1 | 0~2 | R/W | -
automatic 1 manual)
|  | A5_Linkage control method | 0 | 1 |  | R/W | -
68 |  | (0 linkage is invalid, 1 linkage is valid, 2 linkage closure is valid) |  |  | 0~2
69 |  | A6_Electric heating installation method (0 | 0 | 1 | 0~2 | R/W | -
pipes, 1 water tank)
70 |  | A7_Current detection mode (0 does not | 1 | 1 | 0~2 | R/W | -
detect, 1 detects)
71 |  | A8_Water pump interval running time | 0 | 1 | 0~120 | R/W | Hour
|  | b1 _Hydration control method | 0 |  | 0~255 | R/W | -
72 |  | ( 00: Float valve control; 01: Temperature control; 02: Time control ) |  | 1
|  | h 1_Return water control method | 0 |  | 0~255 | R/W | -
73 |  | ( 00: Flow switch control; 01: Temperature difference control; 02: Timing control; 03: Floor |  | 1
heating circulation pump )
74 |  | H0_Defrost parameter setting password | 11 | 1 | 0~99 | R/W | -
75 |  | H1_accumulated running time of compressor | 45 | 1 | 1 0~ 12 | R/W | minu
|  | (defrost) |  |  | 0 |  | te
76 |  | H2_Defrost start temperature | -4 | 1 | -9~9 | R/W | ℃
77 |  | H3_Maximum defrost time | 8 | 1 | 2~18 | R/W | minu
te
address allocation table
default
address |  | content | value | STEP | scope | state | unit
78 |  | H4_Defrost exit temperature | 12 | 1 | 10~30 | R/W | ℃
79 |  | H5_Defrost mode | 1 | 1 | 0-2 | R/W | -
80 |  | H6_defrost time multiple | 10 |  | 0-30 | R/W | -
81 |  | H7_Defrost duration variation coefficient | 0 |  | - 8 ~ 7
82 |  | H8_Defrost mode switching value | 16 |  | - 10~ 2 0
83 |  | H9_Coil and ambient temperature difference | 12 | 1 | 0~20 | R/W | -
1 (-4℃≤T environment)
84 |  | HA_coil and ambient temperature difference | 8 | 1 | 0~ 30 | R/W | -
2 (-20℃≤T environment≤-5℃)
85 |  | HB_coil and ambient temperature difference | 6 | 1 | 0~ 30 | R/W | -
3 (T environment ≤ -21℃)
D1_Model selection
0- single cooling (water inlet, water outlet, room temperature)
1- Single heat (water inlet, water outlet, room temperature, water tank)
2- Cooling and Heating (water inlet, water outlet, room temperature)
3- Low temperature hot water (forced water tank control)
4- Normal temperature hot water (forced water tank control)
86 |  |  | 3 | 1 | 0~4 | R/W | -
87 |  | D2_Crankshaft heating/alarm (0 crankcase | 0 | 1 | 0~1 | R/W | -
heating, 1 alarm)
88 |  | D3_System selection (0: single system; 1: | 1 | 1 | 0~1 | R/W | -
dual system)
89 |  | D4_Fan mode (0 dual motors 1 single fan | 1 | 1 | 0~2 | R/W | -
speed 2 double fan speed)
|  | D5_Fan protection mode (0 does not stop the fan; 1 stops the fan) | 0 | 1 |  | R/W | -
90 |  |  |  |  | 0~1
91 |  | D6_over-current protection upper limit value | 35 | 1 | 5~40 | R/W | A
92 |  | D7_lower limit of over-current protection | 0 | 1 | 0~6 | R/W | A
93 | [5 empty] | R/W | minu
|  | D8_Low voltage start-up detection delay | 0 | 1 | 0~60 |  | te
94 |  | D9_Injection liquid exhaust temperature value | 102 | 1 | 95~150 | R/W | ℃
address allocation table
default
address |  | content | value | STEP | scope | state | unit
DA_temperature control mode
95 |  | (0 water inlet, 1 water outlet, 2 room temperature, 3 water tanks) | 3 | 1 | 0~3 | R/W | -
DB_Liquid injection air supply selection in cooling mode
0- Spraying liquid and replenishing air are working normally
96 |  | 1- Do not use spray liquid or air replenishment | 0 | 1 | 0~1 | R/W | -
97 |  | DC_ -20 degrees maximum operating temperature | 50 | 1 | 20~90 | R/W | ℃
98 |  | DD_ -25 degrees maximum operating temperature | 45 | 1 | 20~90 | R/W | ℃
99 |  | reserved | 0 | 1 | 0~255 | R/W | -
F1_Heating main circuit EXV control mode 0 - superheat
1-Environment 2-Manual
3-Determined opening
100 |  |  | 0 | 1 | 0~3 | R/W | -
101 |  | reserved | 0 | 1 | 0~1 | R/W | -
F2_Heating SV superheat degree set value system 1
102 |  |  | 1 | 1 | -10~10 | R/W | ℃
103 |  | F3_Heating ZB superheat stability zone | 1 | 1 | 0~10 | R/W | ℃
104 |  | F4_Heating AJ adjustment coefficient | 1 | 1 | 1~20 | R/W | -
2
105 |  | F5_Heating initial opening correction value | 0 | 1 | -90~120 | R/W | step s
106 |  | F6_Heating initial opening holding time | 2 |  | 1~10 | R/W | minu
|  |  |  | 1 |  |  | te
|  | F7_Heating main circuit EXV adjustment |  |  |  |  | Seco nd
107 |  | cycle | 30 | 1 | 5~120 | R/W
|  | F8_Heating main circuit EXV minimum opening |  |  |  |  | 2
108 |  |  | 50 | 1 | 1~120 | R/W | step s
2
109 |  | F9_Heating main circuit EXV manual steps | 50 | 1 | 0-250 | R/W | step s
110 |  | FA_heating reserve | 1 | 1 | -90~90 | R/W | ℃
address allocation table
default
address |  | content | value | STEP | scope | state | unit
111 |  | FB_Heating oscillation lock time | 5 | 1 | 0~30 | R/W | cycle
112 |  | L1_ Refrigeration SV superheat setting value | 1 | 1 | -10~10 | R/W | ℃
113 |  | L2_ Refrigeration ZB superheat stability zone | 1 | 1 | 0~10 | R/W | ℃
114 |  | L3_ Refrigeration AJ adjustment coefficient | 1 | 1 | 1~20 | R/W | ℃
2
115 |  | L4_ Refrigeration initial opening correction | 0 | 1 | -90~120 | R/W | step s
116 |  | L5_refrigeration initial opening holding time | 2 |  | 1~10 | R/W | minu
|  |  |  | 1 |  |  | te
|  | L6_refrigeration main circuit EXV adjustment |  |  |  |  | Seco nd
117 |  | cycle | 30 | 1 | 5~120 | R/W
|  | L7_refrigeration main circuit EXV minimum opening |  |  |  |  | 2
118 |  |  | 50 | 1 | 1~120 | R/W | step s
|  | L8_refrigeration main circuit EXV manual steps |  |  |  |  | 2
119 |  |  | 50 | 1 | 0-250 | R/W | step s
L9_ Refrigeration SV superheat degree set
120 |  | value system 2 | 1 | 1 | -90~90 | R/W | ℃
121 |  | LA_ Refrigeration oscillation lock time | 5 | 1 | 0~30 | R/W | cycle
122 |  | LB_EXV exhaust protection value | 110 | 1 | 80~120 | R/W | ℃
LC_EXV exhaust protection opening
123 |  | coefficient | 10 | 1 | 1~30 | R/W
2
124 |  | LD_Heating system 2 minimum opening | 50 | 1 | 1~120 | R/W | step s
|  | LE_Minimum opening of refrigeration system 2 |  |  |  |  | 2
125 |  |  | 50 | 1 | 1~120 | R/W | step s
LF_The proportional value of the minimum opening of the main road that decreases with the ambient temperature when the environment is less than -9
126 |  |  | 20 | 1 | 0~120 | R/W | -
127 |  | N1_auxiliary path EXV control mode | 0 | 1 | 0-6 | R/W
address allocation table
default
address |  | content | value | STEP | scope | state | unit
(0: automatic; 1: manual; 2: Danfoss)
128 |  | reserved | 0 | 1 | 0~1 | R/W | -
|  | N2_auxiliary path EXV exhaust set |  |  |  | R/W
129 |  | temperature | 55 | 1 | 55-105 |  | ℃
|  | N3_auxiliary circuit EXV superheat setting value |  |  |  | R/W
130 |  |  | 3 | 1 | -30 |  | ℃
[6 empty] | R/W | 2
131 |  | N4_auxiliary road EXV initial opening | 40 | 1 | 10-120 |  | step s
132 |  | N5_auxiliary path EXV adjustment cycle | 15 |  | 5-120 | R/W | Seco
|  |  |  | 1 |  |  | nd
[6 empty] | R/W | 2
133 |  | N6_auxiliary road EXV minimum opening | 30 | 1 | 0-120 |  | step s
|  | N7_auxiliary road EXV is forced to open to a large exhaust value A |  |  |  | R/W
134 |  |  | 95 | 1 | 75-150 |  | ℃
|  | N8_auxiliary road EXV is forced to open a |  |  |  | R/W
135 |  | small exhaust value B | 60 | 1 | 40-80 |  | ℃
|  | N9_auxiliary road EXV manual step counting system 1 |  |  |  | R/W | 2
136 |  |  | 50 | 1 | 0-250 |  | step s
|  | NA_auxiliary road manual step counting system 2 |  |  |  |  | 2
137 |  |  | 50 | 1 | 0~250 | R/W | step s
138 |  | NB_auxiliary road EXV spray starting opening | 35 | 1 | 5-150 | R/W | step
Y1_auxiliary line EXV supplementary air exhaust temperature 1
139 |  |  | 110 | 1 | 51-1 5 0 | R/W | ℃
Y2_auxiliary path EXV supplementary air exhaust temperature 2
140 |  |  | 120 | 1 | 51-1 5 0 | R/W | ℃
Y3_auxiliary path EXV supplementary air exhaust temperature 3
141 |  |  | 130 | 1 | 51-1 5 0 | R/W | ℃
Y4_auxiliary path EXV supplementary air exhaust temperature 4
142 |  |  | 105 | 1 | 71-1 5 0 | R/W | ℃
143 |  | Y5_Ambient temperature ≤ -15℃ auxiliary | 35 | 1 | 0-100 | R/W | ℃
address allocation table
default
address |  | content | value | STEP | scope | state | unit
road EXV exhaust temperature difference
Y6_Ambient temperature ≤ -8℃ auxiliary road EXV exhaust temperature difference
144 |  |  | 35 | 1 | 0-100 | R/W | ℃
Y7_Ambient temperature ≤ 0℃ auxiliary path EXV exhaust temperature difference
145 |  |  | 35 | 1 | 0-100 | R/W | ℃
Y 8_Ambient temperature ≥ 1℃ auxiliary path EXV exhaust temperature difference
146 |  |  | 35 | 1 | 0-100 | R/W | ℃
Y9_auxiliary road EXV ambient temperature
147 |  | -15 or below correction 1 | 0 | 1 | -90~90 | R/W | %
YA_auxiliary road EXV ambient temperature
148 |  | -7 or above correction 2 | 0 | 1 | -90~90 | R/W | %
YB_auxiliary road EXV ambient temperature above 0 correction 3
149 |  |  | 0 | 1 | -90~90 | R/W | %
YC_System 2 auxiliary road correction
150 |  | coefficient | 0 | 1 | -90~90 | R/W | %
FC_Heating SV superheat degree set value 2 system 1
151 |  |  | 1 | 1 | -10~10 | R/W | ℃
FD_Heating SV superheat degree set value 3
152 |  | system 1 | 1 | 1 | -10~10 | R/W | ℃
FE_Heating SV superheat degree set value 4 system 1
153 |  |  | 1 | 1 | -10~10 | R/W | ℃
FF_Heating SV superheat setting value 5
154 |  | system 1 | 1 | 1 | -10~10 | R/W | ℃
FP_Heating SV superheat degree set value 2 system 2
155 |  |  | 1 | 1 | -10~10 | R/W | ℃
FN_Heating SV superheat setting value 3
156 |  | system 2 | 1 | 1 | -10~10 | R/W | ℃
FH_Heating SV superheat degree set value 4 system 2
157 |  |  | 1 | 1 | -10~10 | R/W | ℃
FL_Heating SV superheat degree set value 5
158 |  | system 2 | 1 | 1 | -10~10 | R/W | ℃
address allocation table
default
address |  | content | value | STEP | scope | state | unit
2
159 |  | LP_ Main valve opening value during defrost | 240 | 1 | 0~250 | R/W | step s
YD_auxiliary path EXV cooling superheat setting value
160 |  |  | 2 | 1 | -15~15 | R/W | ℃
YE_auxiliary road EXV refrigeration exhaust
161 |  | temperature difference | 50 | 1 | 0~100 | R/W | ℃
162 |  | b2_water input temperature | 45 | 1 | 20~55 | R/W | ℃
b3_water replenishment start and stop temperature difference
163 |  |  | 4 | 1 | 2~20 | R/W | ℃
164 |  | h2_return valve exit temperature | 38 | 1 | 20~55 | R/W | ℃
h3_Return valve opening and closing temperature difference
165 |  |  | 5 | 1 | 2~20 | R/W | ℃
DE_Electronic expansion valve selection 0-Fuji Koki 500 steps
166 |  | 0-Sanhua 500 steps | 0 | 1 | 0~1 | R/W
167 |  | DF_parameter selection | 0 | 1 | 0~29 | R/W