## Sheet1
id | register | name | description | system_category | category | view | sampling | read | write | minvalue | maxvalue | unit | offset | addition | mask | value | length | general_icon | alarm | metadata | l10n | tags | type | parameter_write_byte_position | mqtt | json | current_value | current_error_status | notes | __origen__
| 1 |  | Ambient temperature (signed char) |  |  |  |  | R |  |  |  | ℃ | [17 empty] | Hoja1 (fila 3)
| 2 |  | Inlet water temperature (signed char) |  |  |  |  | R |  |  |  | ℃ | [17 empty] | Hoja1 (fila 3)
| 3 |  | Return water temperature (signed char) |  |  |  |  | R |  |  |  | ℃ | [17 empty] | Hoja1 (fila 3)
| 4 |  | Water tank 1 temperature (signed char) |  |  |  |  | R |  |  |  | ℃ | [17 empty] | Hoja1 (fila 3)
| 5 |  | Coil 1 temperature (signed char) |  |  |  |  | R |  |  |  | ℃ | [17 empty] | Hoja1 (fila 3)
| 6 |  | Coil 2 temperature (signed char) |  |  |  |  | R |  |  |  | ℃ | [17 empty] | Hoja1 (fila 3)
| 7 |  | Suction 1 temperature (signed char) |  |  |  |  | R |  |  |  | ℃ | [17 empty] | Hoja1 (fila 3)
| 8 |  | Suction 2 Temperature (signed char) |  |  |  |  | R |  |  |  | ℃ | [17 empty] | Hoja1 (fila 3)
| 9 |  | Exhaust 1 temperature |  |  |  |  | R |  | 20 | 135 | ℃ | [17 empty] | Hoja1 (fila 3)
| 10 |  | Exhaust 2 temperature |  |  |  |  | R |  | 20 | 135 | ℃ | [17 empty] | Hoja1 (fila 3)
| 11 |  | Cooling inlet 1 temperature |  |  |  |  | R |  |  |  | ℃ | [17 empty] | Hoja1 (fila 3)
| 12 |  | Cooling inlet 2 temperature |  |  |  |  | R |  |  |  | ℃ | [17 empty] | Hoja1 (fila 3)
| 13 |  | Intercooling inlet temperature 1 |  |  |  |  | R |  |  |  | ℃ | [17 empty] | Hoja1 (fila 3)
| 14 |  | Intercooling inlet temperature 2 |  |  |  |  | R |  |  |  | ℃ | [17 empty] | Hoja1 (fila 3)
| 15 |  | Intercooling outlet temperature 1 |  |  |  |  | R |  |  |  | ℃ | [17 empty] | Hoja1 (fila 3)
| 16 |  | Intercooling outlet temperature 2 |  |  |  |  | R |  |  |  | ℃ | [17 empty] | Hoja1 (fila 3)
| 17 |  | (Not used as reserved) |  |  |  |  | R |  | 0 | 255 | ℃ | [17 empty] | Hoja1 (fila 3)
| 18 |  | (Not used as reserved) |  |  |  |  | R |  | 0 | 255 | ℃ | [17 empty] | Hoja1 (fila 3)
| 19 |  | Compressor 1 current |  |  |  |  | R |  | 0 | 255 | - | [17 empty] | Hoja1 (fila 3)
| 20 |  | Compressor 2 current |  |  |  |  | R |  | 0 | 255 | - | [17 empty] | Hoja1 (fila 3)
| 21 |  | Electronic expansion valve opening 1 main circuit |  |  |  |  | R |  | 0 | 255 | - | [17 empty] | Hoja1 (fila 3)
| 22 |  | Electronic expansion valve opening 2 main circuit |  |  |  |  | R |  | 0 | 255 | - | [17 empty] | Hoja1 (fila 3)
| 23 |  | Electronic expansion valve opening 1 auxiliary circuit |  |  |  |  | R |  | 0 | 255 | - | [17 empty] | Hoja1 (fila 3)
| 24 |  | Electronic expansion valve opening 2 auxiliary circuit |  |  |  |  | R |  | 0 | 255 | - | [17 empty] | Hoja1 (fila 3)
| 26 |  | Ambient temperature status (0 normal, 1 fault) |  |  |  |  | R |  |  |  | - | [17 empty] | Hoja1 (fila 34)
|  |  | Inlet water temperature status (0 normal, 1 fault) |  |  |  |  | R |  |  |  | - | [17 empty] | Hoja1 (fila 34)
|  |  | Return water temperature status (0 normal, 1 fault) |  |  |  |  | R |  |  |  | - | [17 empty] | Hoja1 (fila 34)
|  |  | Water tank 1 temperature status (0 normal, 1 fault) |  |  |  |  | R |  |  |  | - | [17 empty] | Hoja1 (fila 34)
|  |  | Coil 1 temperature status (0 normal, 1 fault) |  |  |  |  | R |  |  |  | - | [17 empty] | Hoja1 (fila 34)
|  |  | Coil 2 temperature status (0 normal, 1 fault) |  |  |  |  | R |  |  |  | - | [17 empty] | Hoja1 (fila 34)
|  |  | Suction 1 temperature status (0 normal, 1 fault) |  |  |  |  | R |  |  |  | - | [17 empty] | Hoja1 (fila 34)
|  |  | Suction 2 temperature status (0 normal, 1 fault) |  |  |  |  | R |  |  |  | - | [17 empty] | Hoja1 (fila 34)
| 27 H2 |  | Exhaust 1 temperature status (0 normal, 1 fault) |  |  |  |  | R |  |  |  | - | [17 empty] | Hoja1 (fila 34)
|  |  | Exhaust 2 temperature status (0 normal, 1 fault) |  |  |  |  | R |  |  |  | - | [17 empty] | Hoja1 (fila 34)
|  |  | Cooling inlet 1 temperature state (0 normal, 1 fault) |  |  |  |  | R |  |  |  | - | [17 empty] | Hoja1 (fila 34)
|  |  | Cooling inlet 2 temperature states (0 normal, 1 fault) |  |  |  |  | R |  |  |  | - | [17 empty] | Hoja1 (fila 34)
|  |  | Intercooling inlet temperature 1 status (0 normal, 1 fault) |  |  |  |  | R |  |  |  | - | [17 empty] | Hoja1 (fila 34)
|  |  | Intercooling inlet temperature 2 status (0 normal, 1 fault) |  |  |  |  | R |  |  |  | - | [17 empty] | Hoja1 (fila 34)
|  |  | Intercooler outlet temperature 1 status (0 normal, 1 fault) |  |  |  |  | R |  |  |  | - | [17 empty] | Hoja1 (fila 34)
|  |  | Intercooler outlet temperature 2 status (0 normal, 1 fault) |  |  |  |  | R |  |  |  | - | [17 empty] | Hoja1 (fila 34)
| 28 H3 |  | Outlet water temperature is too high fault (0 normal, normal, 1 fault) |  |  |  |  | R |  |  |  | - | [17 empty] | Hoja1 (fila 34)
|  |  | Outlet water temperature is too low fault (0 normal, 1 fault) |  |  |  |  | R |  |  |  | - | [17 empty] | Hoja1 (fila 34)
|  |  | Reserved (0 normal, 1 fault) |  |  |  |  | R |  |  |  | - | [17 empty] | Hoja1 (fila 34)
|  |  | Reserved (0 normal, 1 fault) |  |  |  |  | R |  |  |  | - | [17 empty] | Hoja1 (fila 34)
|  |  | Reserved (0 normal, 1 fault) |  |  |  |  | R |  |  |  | - | [17 empty] | Hoja1 (fila 34)
|  |  | Undervoltage and overvoltage fault (0 |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 61)
|  |  | normal, 1 fault) | [26 empty] | Hoja1 (fila 61)
|  |  | Cooling inlet 1 low temperature state (0 |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 61)
|  |  | normal, 1 fault) | [26 empty] | Hoja1 (fila 61)
|  |  | Cooling inlet 2 low temperature status (0 |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 61)
|  |  | normal, 1 fault) | [26 empty] | Hoja1 (fila 61)
|  |  | Low pressure switch 1 (0 normal, 1 fault) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 61)
|  |  | Low pressure switch 2 (0 normal, 1 fault) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 61)
|  |  | Low pressure switch 3 (0 normal, 1 fault) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 61)
|  |  | Low pressure switch 4 (0 normal, 1 fault) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 61)
| 29 |  | High pressure switch 1 (0 normal, 1 fault) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 61)
| H4 |  | High pressure switch 2 (0 normal, 1 fault) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 61)
|  |  | High pressure switch 3 (0 normal, 1 fault) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 61)
|  |  | High pressure switch 4 (0 normal, 1 fault) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 61)
|  |  | Overcurrent switch 1 (0 normal, 1 fault) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 61)
|  |  | Overcurrent switch 2 (0 normal, 1 fault) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 61)
|  |  | Overcurrent switch 3 (0 normal, 1 fault) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 61)
|  |  | Overcurrent switch 4 (0 normal, 1 fault) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 61)
|  |  | Exhaust protection 1 (0 normal, 1 fault) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 61)
| 30 |  | Exhaust protection 2 (0 normal, 1 fault) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 61)
| H5 |  | Exhaust protection 3 (0 normal, 1 fault) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 61)
|  |  | Exhaust protection 4 (0 normal, 1 fault) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 61)
|  |  | The temperature difference between water |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 61)
|  |  | inlet and outlet is too high (0 normal, 1 fault) | [26 empty] | Hoja1 (fila 61)
|  |  | Phase loss or reverse phase (0 normal, 1 |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 61)
|  |  | fault) | [26 empty] | Hoja1 (fila 61)
|  |  | Water flow switch (0 normal, 1 fault) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 61)
| 31 |  | Water pressure switch (0 normal, 1 fault) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 61)
| H6 |  | Low water level switch (0 normal, 1 fault) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 61)
|  |  | High water level switch (0 normal, 1 fault) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 61)
|  |  | Outlet water temperature is too low (0 |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 61)
|  |  | normal, 1 fault) | [26 empty] | Hoja1 (fila 61)
|  |  | (Not used as reserved) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 61)
|  |  | (Not used as reserved) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 61)
| 32 |  | (Not used as reserved) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 61)
| H7 |  | (Not used as reserved) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 61)
|  |  | (Not used as reserved) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 61)
|  |  | (Not used as reserved) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 102)
|  |  | (Not used as reserved) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 102)
|  |  | (Not used as reserved) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 102)
|  |  | (Not used as reserved) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 102)
|  |  | (Not used as reserved) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 102)
|  |  | (Not used as reserved) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 102)
|  |  | (Not used as reserved) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 102)
|  |  | (Not used as reserved) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 102)
| 33 |  | (Not used as reserved) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 102)
| H8 |  | (Not used as reserved) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 102)
|  |  | (Not used as reserved) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 102)
|  |  | (Not used as reserved) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 102)
|  |  | Linkage switch (0 normal, 1 fault) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 102)
|  |  | Reverse phase status (0 normal, 1 fault) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 102)
|  |  | Phase loss B status (0 normal, 1 fault) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 102)
|  |  | Phase loss C status (0 normal, 1 fault) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 102)
|  |  | There is a fault lock that needs to alarm (0 |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 102)
|  |  | normal, 1 fault) | [26 empty] | Hoja1 (fila 102)
| 34 |  | (Not used as reserved) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 102)
| H9 |  | (Not used as reserved) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 102)
|  |  | (Not used as reserved) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 102)
|  |  | The quality of EE24C02 (0 normal, 1 fault) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 102)
|  |  | Defrost (0 is not present, 1 is present) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 102)
|  |  | Antifreeze (0 is not present, 1 is present) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 102)
|  |  | Communication status (0 normal, 1 fault) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 102)
| 35 |  | (Not used as reserved) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 102)
| H10 |  | (Not used as reserved) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 102)
|  |  | (Not used as reserved) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 102)
|  |  | (Not used as reserved) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 102)
|  |  | Compressor 1 (0 off, 1 on) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 102)
|  |  | Compressor 2 (0 off, 1 on) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 102)
| 36 |  | Compressor 3 (0 off, 1 on) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 102)
| R1 |  | Compressor 4 (0 off, 1 on) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 102)
|  |  | 4-way valve 1 (0 closes, 1 opens) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 102)
|  |  | Fan high speed (0 off, 1 on) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 102)
|  |  | Fan low speed(0 off, 1 on) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 141)
|  |  | Circulation pump (0 off, 1 on) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 141)
|  |  | Water pump (0 off, 1 on) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 141)
|  |  | Water return valve (0 closes, 1 opens) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 141)
|  |  | Auxiliary electric heater power (0 turns off, 1 |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 141)
|  |  | turns on) | [26 empty] | Hoja1 (fila 141)
| 37 |  | Alarm (0 off, 1 on) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 141)
| R2 |  | Spray valve 1 (0 closes, 1 opens) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 141)
|  |  | Spray valve 2 (0 closes, 1 opens) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 141)
|  |  | Spray valve 3 (0 closes, 1 opens) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 141)
|  |  | Spray valve 4 (0 closes, 1 opens) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 141)
|  |  | (Not used as reserved) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 141)
|  |  | (Not used as reserved) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 141)
|  |  | (Not used as reserved) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 141)
|  |  | (Not used as reserved) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 141)
| 38 |  | (Not used as reserved) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 141)
| R3 |  | (Not used as reserved) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 141)
|  |  | (Not used as reserved) |  |  |  |  | R |  | 0 | 1 | - | [17 empty] | Hoja1 (fila 141)
|  |  | (Not used as reserved) | [26 empty] | Hoja1 (fila 141)
| 39 |  | Heating set temperature |  |  |  |  | R | W | 5 | 60 | - | [17 empty] | Hoja1 (fila 141)
| 40 |  | command reservation |  |  |  |  | R | W | 0 | 255 | [18 empty] | Hoja1 (fila 141)
| 41 |  | System operating mode (0 cooling, 1 heating) |  |  |  |  | R | W | 0 | 255 | [18 empty] | Hoja1 (fila 141)
| 42 |  | command reservation |  |  |  |  | R | W | 0 | 255 | [18 empty] | Hoja1 (fila 141)
| 43 |  | Cooling set temperature |  |  |  |  | R | W | 10 | 35 | [18 empty] | Hoja1 (fila 141)
| 44 |  | command reservation |  |  |  |  | R | W | 0 | 255 | [18 empty] | Hoja1 (fila 141)
|  |  | Power on/off command (0 to turn off, 1 to |  |  |  |  | R | W | 0 | 1 | - | [17 empty] | Hoja1 (fila 141)
|  |  | turn on) | [26 empty] | Hoja1 (fila 141)
|  |  | Manual electric heating command (0 off, 1 |  |  |  |  | R | W | 0 | 1 | - | [17 empty] | Hoja1 (fila 141)
|  |  | on) | [26 empty] | Hoja1 (fila 141)
| 45 |  | command reservation |  |  |  |  | R | W | 0 | 1 | - | [17 empty] | Hoja1 (fila 141)
|  |  | command reservation |  |  |  |  | R | W | 0 | 1 | - | [17 empty] | Hoja1 (fila 141)
|  |  | command reservation |  |  |  |  | R | W | 0 | 1 | - | [17 empty] | Hoja1 (fila 141)
|  |  | command reservation |  |  |  |  | R | W | 0 | 1 | - | [17 empty] | Hoja1 (fila 141)
|  |  | command reservation |  |  |  |  | R | W | 0 | 1 | - | [17 empty] | Hoja1 (fila 141)
|  |  | command reservation |  |  |  |  | R | W | 0 | 1 | - | [17 empty] | Hoja1 (fila 180)
|  |  | command reservation |  |  |  |  | R | W | 0 | 1 | - | [17 empty] | Hoja1 (fila 180)
|  |  | command reservation |  |  |  |  | R | W | 0 | 1 | - | [17 empty] | Hoja1 (fila 180)
|  |  | command reservation |  |  |  |  | R | W | 0 | 1 | - | [17 empty] | Hoja1 (fila 180)
|  |  | command reservation |  |  |  |  | R | W | 0 | 1 | - | [17 empty] | Hoja1 (fila 180)
| 46 |  | command reservation |  |  |  |  | R | W | 0 | 1 | - | [17 empty] | Hoja1 (fila 180)
|  |  | command reservation |  |  |  |  | R | W | 0 | 1 | - | [17 empty] | Hoja1 (fila 180)
|  |  | command reservation |  |  |  |  | R | W | 0 | 1 | - | [17 empty] | Hoja1 (fila 180)
|  |  | command reservation | [26 empty] | Hoja1 (fila 180)
|  |  | command reservation |  |  |  |  | R | W | 0 | 1 | - | [17 empty] | Hoja1 (fila 180)
|  |  | Forced defrost command (0 off, 1 on) |  |  |  |  | R | W | 0 | 1 | - | [17 empty] | Hoja1 (fila 180)
|  |  | command reservation |  |  |  |  | R | W | 0 | 1 | - | [17 empty] | Hoja1 (fila 180)
|  |  | command reservation |  |  |  |  | R | W | 0 | 1 | - | [17 empty] | Hoja1 (fila 180)
|  |  | command reservation |  |  |  |  | R | W | 0 | 1 | - | [17 empty] | Hoja1 (fila 180)
| 47 |  | command reservation |  |  |  |  | R | W | 0 | 1 | - | [17 empty] | Hoja1 (fila 180)
|  |  | command reservation |  |  |  |  | R | W | 0 | 1 | - | [17 empty] | Hoja1 (fila 180)
|  |  | command reservation |  |  |  |  | R | W | 0 | 1 | - | [17 empty] | Hoja1 (fila 180)
| 48 |  | command reservation | [26 empty] | Hoja1 (fila 180)
| 49 |  | C1_compressor start and stop temperature |  |  |  |  | R | W | 2 | 20 | ℃ | [17 empty] | Hoja1 (fila 180)
|  |  | difference | [26 empty] | Hoja1 (fila 180)
| 50 |  | C2_Energy level detection cycle |  |  |  |  | R | W | 0 | 50 | ℃ | [17 empty] | Hoja1 (fila 180)
| 51 |  | C3_ Outlet water temperature is too high |  |  |  |  | R | W | 50 | 80 | ℃ | [17 empty] | Hoja1 (fila 180)
|  |  | protection | [26 empty] | Hoja1 (fila 180)
| 52 |  | C4_ Outlet water temperature is too low |  |  |  |  | R | W | 2 | 10 | ℃ | [17 empty] | Hoja1 (fila 180)
|  |  | protection | [26 empty] | Hoja1 (fila 180)
| 53 |  | C5_Inlet and outlet water temperature |  |  |  |  | R | W | 5 | 50 | ℃ | [17 empty] | Hoja1 (fila 180)
|  |  | difference protection | [26 empty] | Hoja1 (fila 180)
| 54 |  | C6_Inlet water temperature correction |  |  |  |  | R | W |  |  | ℃ | [17 empty] | Hoja1 (fila 180)
| 55 |  | C7_ambient temperature for auxiliary |  |  |  |  | R | W |  |  | ℃ | [17 empty] | Hoja1 (fila 180)
|  |  | electric heater automatically start | [26 empty] | Hoja1 (fila 180)
| 56 |  | C8_enthalpy increasing input temperature |  |  |  |  | R | W |  |  | ℃ | [17 empty] | Hoja1 (fila 180)
| 57 |  | C9_enthalpy increase input temperature |  |  |  |  | R | W | 1 | 10 | ℃ | [17 empty] | Hoja1 (fila 180)
|  |  | difference | [26 empty] | Hoja1 (fila 180)
| 58 |  | CA_Ambient temperature for fan speed |  |  |  |  | R | W |  |  | ℃ | [17 empty] | Hoja1 (fila 180)
|  |  | switching | [26 empty] | Hoja1 (fila 180)
| 59 |  | CB_ambient temperature for heating tape |  |  |  |  | R | W |  |  | ℃ | [17 empty] | Hoja1 (fila 221)
|  |  | start (defrost electric heating) | [26 empty] | Hoja1 (fila 221)
| 60 |  | CC_Heating tape running time (defrost |  |  |  |  | R | W |  |  | MIN | [17 empty] | Hoja1 (fila 221)
|  |  | electric heating) | [26 empty] | Hoja1 (fila 221)
| 61 |  | CD_exhaust protection temperature value |  |  |  |  | R | W |  |  | ℃ | [17 empty] | Hoja1 (fila 221)
| 62 |  | CE_ambient temperature set value |  |  |  |  | R | W | 10 | 35 | ℃ | [17 empty] | Hoja1 (fila 221)
| 63 |  | CF_ambient temperature difference |  |  |  |  | R | W | 2 | 10 | ℃ | [17 empty] | Hoja1 (fila 221)
| 78 |  | H4_Defrost exit temperature |  |  |  |  | R | W | 10 | 30 | ℃ | [17 empty] | Hoja1 (fila 259)
| 79 |  | H5_Defrost mode |  |  |  |  | R | W | 0 | 2 | - | [17 empty] | Hoja1 (fila 259)
| 80 |  | H6_defrost time multiple |  |  |  |  | R | W | 0 | 30 | - | [17 empty] | Hoja1 (fila 259)
| 81 |  | H7_Defrost duration variation coefficient | [26 empty] | Hoja1 (fila 259)
| 82 |  | H8_Defrost mode switching value | [26 empty] | Hoja1 (fila 259)
| 83 |  | H9_Coil and ambient temperature difference |  |  |  |  | R | W | 0 | 20 | - | [17 empty] | Hoja1 (fila 259)
|  |  | 1 (-4℃≤T environment) | [26 empty] | Hoja1 (fila 259)
| 84 |  | HA_coil and ambient temperature difference |  |  |  |  | R | W | 0 | 30 | - | [17 empty] | Hoja1 (fila 259)
|  |  | 2 (-20℃≤T environment≤-5℃) | [26 empty] | Hoja1 (fila 259)
| 85 |  | HB_coil and ambient temperature difference |  |  |  |  | R | W | 0 | 30 | - | [17 empty] | Hoja1 (fila 259)
|  |  | 3 (T environment ≤ -21℃) | [26 empty] | Hoja1 (fila 259)
|  |  | DA_temperature control mode | [26 empty] | Hoja1 (fila 295)
| 95 |  | (0 water inlet, 1 water outlet, 2 room temperature, 3 water tanks) |  |  |  |  | R | W | 0 | 3 | - | [17 empty] | Hoja1 (fila 295)
|  |  | DB_Liquid injection air supply selection in cooling mode | [26 empty] | Hoja1 (fila 295)
|  |  | 0- Spraying liquid and replenishing air are working normally | [26 empty] | Hoja1 (fila 295)
| 96 |  | 1- Do not use spray liquid or air replenishment |  |  |  |  | R | W | 0 | 1 | - | [17 empty] | Hoja1 (fila 295)
| 97 |  | DC_ -20 degrees maximum operating temperature |  |  |  |  | R | W | 20 | 90 | ℃ | [17 empty] | Hoja1 (fila 295)
| 98 |  | DD_ -25 degrees maximum operating temperature |  |  |  |  | R | W | 20 | 90 | ℃ | [17 empty] | Hoja1 (fila 295)
| 99 |  | reserved |  |  |  |  | R | W | 0 | 255 | - | [17 empty] | Hoja1 (fila 295)
| 111 |  | FB_Heating oscillation lock time |  |  |  |  | R | W | 0 | 30 | cycle | [17 empty] | Hoja1 (fila 328)
| 112 |  | L1_ Refrigeration SV superheat setting value |  |  |  |  | R | W |  |  | ℃ | [17 empty] | Hoja1 (fila 328)
| 113 |  | L2_ Refrigeration ZB superheat stability zone |  |  |  |  | R | W | 0 | 10 | ℃ | [17 empty] | Hoja1 (fila 328)
| 114 |  | L3_ Refrigeration AJ adjustment coefficient | [8 empty] | 2 | [17 empty] | Hoja1 (fila 328)
| 115 |  | L4_ Refrigeration initial opening correction |  |  |  |  | R | W |  |  | step s | [17 empty] | Hoja1 (fila 328)
| 116 |  | L5_refrigeration initial opening holding time | [8 empty] | te | [17 empty] | Hoja1 (fila 328)
|  |  | L6_refrigeration main circuit EXV adjustment | [8 empty] | Seco nd | [17 empty] | Hoja1 (fila 328)
| 117 |  | cycle |  |  |  |  | R | W | 5 | 120 | [18 empty] | Hoja1 (fila 328)
|  |  | L7_refrigeration main circuit EXV minimum opening |  |  |  |  | R | W | 1 | 120 | step s | [17 empty] | Hoja1 (fila 328)
|  |  | L8_refrigeration main circuit EXV manual steps |  |  |  |  | R | W | 0 | 250 | step s | [17 empty] | Hoja1 (fila 328)
|  |  | L9_ Refrigeration SV superheat degree set | [26 empty] | Hoja1 (fila 328)
| 120 |  | value system 2 |  |  |  |  | R | W |  |  | ℃ | [17 empty] | Hoja1 (fila 328)
| 121 |  | LA_ Refrigeration oscillation lock time |  |  |  |  | R | W | 0 | 30 | cycle | [17 empty] | Hoja1 (fila 328)
| 122 |  | LB_EXV exhaust protection value |  |  |  |  | R | W | 80 | 120 | ℃ | [17 empty] | Hoja1 (fila 328)
|  |  | LC_EXV exhaust protection opening | [26 empty] | Hoja1 (fila 328)
| 123 |  | coefficient | [8 empty] | 2 | [17 empty] | Hoja1 (fila 328)
| 124 |  | LD_Heating system 2 minimum opening |  |  |  |  | R | W | 1 | 120 | step s | [17 empty] | Hoja1 (fila 328)
|  |  | LE_Minimum opening of refrigeration system 2 |  |  |  |  | R | W | 1 | 120 | step s | [17 empty] | Hoja1 (fila 328)
|  |  | LF_The proportional value of the minimum opening of the main road that decreases with the ambient temperature when the environment is less than -9 | [26 empty] | Hoja1 (fila 328)
|  |  | (0: automatic; 1: manual; 2: Danfoss) | [26 empty] | Hoja1 (fila 361)
| 128 |  | reserved |  |  |  |  | R | W | 0 | 1 | - | [17 empty] | Hoja1 (fila 361)
|  |  | N2_auxiliary path EXV exhaust set |  |  |  |  | R | W | [20 empty] | Hoja1 (fila 361)
| 129 |  | temperature | [6 empty] | 55 | 105 | ℃ | [17 empty] | Hoja1 (fila 361)
|  |  | N3_auxiliary circuit EXV superheat setting value | [8 empty] | ℃ | [17 empty] | Hoja1 (fila 361)
| 131 |  | N4_auxiliary road EXV initial opening | [6 empty] | 10 | 120 | step s | [17 empty] | Hoja1 (fila 361)
| 132 |  | N5_auxiliary path EXV adjustment cycle | [8 empty] | nd | [17 empty] | Hoja1 (fila 361)
| 133 |  | N6_auxiliary road EXV minimum opening | [6 empty] | 0 | 120 | step s | [17 empty] | Hoja1 (fila 361)
|  |  | N7_auxiliary road EXV is forced to open to a large exhaust value A | [6 empty] | 75 | 150 | ℃ | [17 empty] | Hoja1 (fila 361)
|  |  | N8_auxiliary road EXV is forced to open a |  |  |  |  | R | W | [20 empty] | Hoja1 (fila 361)
| 135 |  | small exhaust value B | [6 empty] | 40 | 80 | ℃ | [17 empty] | Hoja1 (fila 361)
|  |  | N9_auxiliary road EXV manual step counting system 1 | [6 empty] | 0 | 250 | step s | [17 empty] | Hoja1 (fila 361)
|  |  | NA_auxiliary road manual step counting system 2 |  |  |  |  | R | W | 0 | 250 | step s | [17 empty] | Hoja1 (fila 361)
| 138 |  | NB_auxiliary road EXV spray starting opening |  |  |  |  | R | W | 5 | 150 | step | [17 empty] | Hoja1 (fila 361)
|  |  | Y1_auxiliary line EXV supplementary air exhaust temperature 1 |  |  |  |  | R | W |  |  | ℃ | [17 empty] | Hoja1 (fila 361)
|  |  | Y2_auxiliary path EXV supplementary air exhaust temperature 2 |  |  |  |  | R | W |  |  | ℃ | [17 empty] | Hoja1 (fila 361)
|  |  | Y3_auxiliary path EXV supplementary air exhaust temperature 3 |  |  |  |  | R | W |  |  | ℃ | [17 empty] | Hoja1 (fila 361)
|  |  | Y4_auxiliary path EXV supplementary air exhaust temperature 4 |  |  |  |  | R | W |  |  | ℃ | [17 empty] | Hoja1 (fila 361)
| 143 |  | Y5_Ambient temperature ≤ -15℃ auxiliary |  |  |  |  | R | W | 0 | 100 | ℃ | [17 empty] | Hoja1 (fila 361)
|  |  | road EXV exhaust temperature difference | [26 empty] | Hoja1 (fila 395)
|  |  | Y6_Ambient temperature ≤ -8℃ auxiliary road EXV exhaust temperature difference |  |  |  |  | R | W | 0 | 100 | ℃ | [17 empty] | Hoja1 (fila 395)
|  |  | Y7_Ambient temperature ≤ 0℃ auxiliary path EXV exhaust temperature difference |  |  |  |  | R | W | 0 | 100 | ℃ | [17 empty] | Hoja1 (fila 395)
|  |  | Y 8_Ambient temperature ≥ 1℃ auxiliary path EXV exhaust temperature difference |  |  |  |  | R | W | 0 | 100 | ℃ | [17 empty] | Hoja1 (fila 395)
|  |  | Y9_auxiliary road EXV ambient temperature | [26 empty] | Hoja1 (fila 395)
| 147 |  | -15 or below correction 1 |  |  |  |  | R | W |  |  | % | [17 empty] | Hoja1 (fila 395)
|  |  | YA_auxiliary road EXV ambient temperature | [26 empty] | Hoja1 (fila 395)
| 148 |  | -7 or above correction 2 |  |  |  |  | R | W |  |  | % | [17 empty] | Hoja1 (fila 395)
|  |  | YB_auxiliary road EXV ambient temperature above 0 correction 3 |  |  |  |  | R | W |  |  | % | [17 empty] | Hoja1 (fila 395)
|  |  | YC_System 2 auxiliary road correction | [26 empty] | Hoja1 (fila 395)
| 150 |  | coefficient |  |  |  |  | R | W |  |  | % | [17 empty] | Hoja1 (fila 395)
|  |  | FC_Heating SV superheat degree set value 2 system 1 |  |  |  |  | R | W |  |  | ℃ | [17 empty] | Hoja1 (fila 395)
|  |  | FD_Heating SV superheat degree set value 3 | [26 empty] | Hoja1 (fila 395)
| 152 |  | system 1 |  |  |  |  | R | W |  |  | ℃ | [17 empty] | Hoja1 (fila 395)
|  |  | FE_Heating SV superheat degree set value 4 system 1 |  |  |  |  | R | W |  |  | ℃ | [17 empty] | Hoja1 (fila 395)
|  |  | FF_Heating SV superheat setting value 5 | [26 empty] | Hoja1 (fila 395)
| 154 |  | system 1 |  |  |  |  | R | W |  |  | ℃ | [17 empty] | Hoja1 (fila 395)
|  |  | FP_Heating SV superheat degree set value 2 system 2 |  |  |  |  | R | W |  |  | ℃ | [17 empty] | Hoja1 (fila 395)
|  |  | FN_Heating SV superheat setting value 3 | [26 empty] | Hoja1 (fila 395)
| 156 |  | system 2 |  |  |  |  | R | W |  |  | ℃ | [17 empty] | Hoja1 (fila 395)
|  |  | FH_Heating SV superheat degree set value 4 system 2 |  |  |  |  | R | W |  |  | ℃ | [17 empty] | Hoja1 (fila 395)
|  |  | FL_Heating SV superheat degree set value 5 | [26 empty] | Hoja1 (fila 395)
| 158 |  | system 2 |  |  |  |  | R | W |  |  | ℃ | [17 empty] | Hoja1 (fila 395)
| 159 |  | LP_ Main valve opening value during defrost |  |  |  |  | R | W | 0 | 250 | step s | [17 empty] | Hoja1 (fila 430)
|  |  | YD_auxiliary path EXV cooling superheat setting value |  |  |  |  | R | W |  |  | ℃ | [17 empty] | Hoja1 (fila 430)
|  |  | YE_auxiliary road EXV refrigeration exhaust | [26 empty] | Hoja1 (fila 430)
| 161 |  | temperature difference |  |  |  |  | R | W | 0 | 100 | ℃ | [17 empty] | Hoja1 (fila 430)
| 162 |  | b2_water input temperature |  |  |  |  | R | W | 20 | 55 | ℃ | [17 empty] | Hoja1 (fila 430)
|  |  | b3_water replenishment start and stop temperature difference |  |  |  |  | R | W | 2 | 20 | ℃ | [17 empty] | Hoja1 (fila 430)
| 164 |  | h2_return valve exit temperature |  |  |  |  | R | W | 20 | 55 | ℃ | [17 empty] | Hoja1 (fila 430)
|  |  | h3_Return valve opening and closing temperature difference |  |  |  |  | R | W | 2 | 20 | ℃ | [17 empty] | Hoja1 (fila 430)
|  |  | DE_Electronic expansion valve selection 0-Fuji Koki 500 steps | [26 empty] | Hoja1 (fila 430)
| 166 |  | 0-Sanhua 500 steps |  |  |  |  | R | W | 0 | 1 | [18 empty] | Hoja1 (fila 430)
| 167 |  | DF_parameter selection |  |  |  |  | R | W | 0 | 29 | [18 empty] | Hoja1 (fila 430)