## processed
id | register | name | description | system_category | category | view | sampling | read | write | minvalue | maxvalue | unit | offset | addition | mask | value | length | general_icon | alarm | metadata | l10n | tags | type | parameter_write_byte_position | mqtt | json | current_value | current_error_status | notes
1 | 1 | CAL_AIRE_VOC | Calidad Aire VOC | STATUS |  | basic | 60 | 4 | 0 | -3276.8 | 3276.7 | % |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"VOC level"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Calidad Aire VOC"}}} | [] | modbus
2 | 2 | CONSIGNA_AUTO | Consigna Modo Auto | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -99.9 | 99.9 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Temperature Control Setpoint"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna Modo Auto"}}} | [] | modbus
3 | 3 | CONSIGNA_CALOR_CONFORT | Consigna Calor Confort | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -999.9 | 999.9 | °C |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Setpoint Confor Heat"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna Calor Confort"}}} | [] | modbus
4 | 4 | CONSIGNA_CALOR_ECO | Consigna Calor Eco | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -999.9 | 999.9 | °C |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Setpoint Eco Heat"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna Calor Eco"}}} | [] | modbus
5 | 5 | CONSIGNA_FRIO_CONFORT | Consigna Frío Confort | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -999.9 | 999.9 | °C |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Setpoint Confor Cool"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna Frío Confort"}}} | [] | modbus
6 | 6 | CONSIGNA_FRIO_ECO | Consigna Frio Eco | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -999.9 | 999.9 | °C |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Setpoint Eco Cool"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna Frio Eco"}}} | [] | modbus
7 | 7 | CONSIGNA_HUMEDAD | Consigna Humedad | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 100 | % |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Humidity Control Setpoint"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna Humedad"}}} | [] | modbus
8 | 8 | HUMEDAD_EXT | Valor Humedad Exterior | STATUS |  | basic | 60 | 4 | 0 | -3276.8 | 3276.7 | % |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Outdoor humidity"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Valor Humedad Exterior"}}} | [] | modbus
9 | 9 | HUMEDAD_IMP | Valor Humedad Impulsión | STATUS |  | basic | 60 | 4 | 0 | -3276.8 | 3276.7 | % |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Supply humidity"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Valor Humedad Impulsión"}}} | [] | modbus
10 | 10 | HUMEDAD_INT | Valor Humedad Interior | STATUS |  | basic | 60 | 4 | 0 | 0 | 99.9 | % |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Ambient humidity"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Valor Humedad Interior"}}} | [] | modbus
11 | 11 | HUMEDAD_POST | Valor Humedad Post Bateria | STATUS |  | basic | 60 | 4 | 0 | -3276.8 | 3276.7 | % |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Post-coil humidity"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Valor Humedad Post Bateria"}}} | [] | modbus
12 | 12 | PRESS_COND_CIRC_1 | Presión Condensador Circuito 1 | STATUS |  | basic | 60 | 4 | 0 | -3276.8 | 3276.7 | BAR |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Condensator pressure circuit 1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Presión Condensador Circuito 1"}}} | [] | modbus
13 | 13 | PRESS_COND_CIRC_2 | Presión Condensador Circuito 2 | STATUS |  | basic | 60 | 4 | 0 | -3276.8 | 3276.7 | BAR |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Condensator pressure circuit 2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Presión Condensador Circuito 2"}}} | [] | modbus
14 | 15 | PRESS_COND_CIRC_REC | Presión Condensador Circuito Recuperación | STATUS |  | basic | 60 | 4 | 0 | -3276.8 | 3276.7 | BAR |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Condensator pressure recovery circuit"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Presión Condensador Circuito Recuperación"}}} | [] | modbus
15 | 16 | TEMP_EXT | Temperatura Exterior | STATUS |  | basic | 60 | 4 | 0 | -3276.8 | 3276.7 | °C |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Outdoor temp."},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura Exterior"}}} | [] | modbus
16 | 17 | TEMP_IMPULSION | Temperatura Impulsión | STATUS |  | basic | 60 | 4 | 0 | -3276.8 | 3276.7 | °C |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Supply temp."},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura Impulsión"}}} | [] | modbus
17 | 18 | TEMP_MEZCLA | Temperatura Mezcla | STATUS |  | basic | 60 | 4 | 0 | -3276.8 | 3276.7 | °C |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Mixing temp."},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura Mezcla"}}} | [] | modbus
18 | 19 | TEMP_RET_AMB | Temperatura Retorno / Ambiente | STATUS |  | basic | 60 | 4 | 0 | -3276.7 | 3276.7 | °C |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"T.Return/Ambient "},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura Retorno / Ambiente"}}} | [] | modbus
19 | 20 | TEMP_POST | Temperatura Post-Batería | STATUS |  | basic | 60 | 4 | 0 | -3276.8 | 3276.7 | % |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Post-coil temp."},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura Post-Batería"}}} | [] | modbus
20 | 21 | Power_L_SPV | Potencia Eléctrica Equivalente calculada por Medidor de Ener | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 999.9 | kW |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Equivalent Electrical Power calculated by Energy Meter when "},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Potencia Eléctrica Equivalente calculada por Medidor de Ener"}}} | [] | modbus
21 | 23 | Min_Ext_Damper | Mínima Apertura Compuerta Exterior expulsión | DAMPERS |  | simple | 0 | 3 | 6 | 0 | 100 | % |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Minimum Opening Outer Exhaust Damper"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Mínima Apertura Compuerta Exterior expulsión"}}} | [] | modbus
22 | 28 | DIF_HUM | Diferencial Humedad | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 100 | % |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Dif.Humidity"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Diferencial Humedad"}}} | [] | modbus
23 | 29 | DIF_FRIO | Diferencial Frío: sumatorio de los difereneciales de los el | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -99.9 | 99.9 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Cold differential: Sum of the differentials of the elements "},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Diferencial Frío: sumatorio de los difereneciales de los el"}}} | [] | modbus
24 | 30 | DIF_CALOR | Diferencial Calor: sumatorio de los difereneciales de los | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -99.9 | 99.9 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Heat differential: Sum of the differentials of the elements "},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Diferencial Calor: sumatorio de los difereneciales de los"}}} | [] | modbus
25 | 31 | Min_Set_Temp_Cool | Mínimo Consigna Frío | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 3276.7 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Cooling setpoint limit Minimun"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Mínimo Consigna Frío"}}} | [] | modbus
26 | 32 | Max_Set_Temp_Cool | Máximo Consigna Frío | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -3276.8 | 3276.7 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Cooling setpoint limit Maximun"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Máximo Consigna Frío"}}} | [] | modbus
27 | 33 | Min_Set_Temp_Heat | Mínimo Consigna Calor | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -3276.8 | 3276.7 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Heating setpoint limit Minimun"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Mínimo Consigna Calor"}}} | [] | modbus
28 | 34 | Max_Set_Temp_Heat | Máximo Consigna Calor | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -3276.8 | 3276.7 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Heating setpoint limit Maximun"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Máximo Consigna Calor"}}} | [] | modbus
29 | 35 | Delta_Temp | Delta Temperatura Activación Free-Cooling | DAMPERS |  | simple | 0 | 3 | 6 | 0 | 99.9 | °C |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Dampers settings Freecool."},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Delta Temperatura Activación Free-Cooling"}}} | [] | modbus
30 | 36 | Diff_Enth | Diferencial Entalpía Compuertas | DAMPERS |  | simple | 0 | 3 | 6 | 0 | 99.9 | kJ/kg |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Dif.Enthalphy dampers"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Diferencial Entalpía Compuertas"}}} | [] | modbus
31 | 37 | Enthalpy_Diff_ON | Diferencial Entalpía On | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 99 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Dif.Enthalphy On"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Diferencial Entalpía On"}}} | [] | modbus
32 | 38 | Set_External_Temp_Inf | Limite mínimo de Temperatura exterior para apertura compuert | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -999.9 | 999.9 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Minimum outdoor temperature limit for opening of renovation "},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Limite mínimo de Temperatura exterior para apertura compuert"}}} | [] | modbus
33 | 39 | Set_External_Temp_Sup | Limite máximo de Temperatura exterior para apertura compuert | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -999.9 | 999.9 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Maximum outdoor temperature limit for opening of renovation "},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Limite máximo de Temperatura exterior para apertura compuert"}}} | [] | modbus
34 | 40 | DIF_COMPUERTA_CALOR | Diferencial Compuerta Calor | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -99.9 | 99.9 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Dif.Heat damper"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Diferencial Compuerta Calor"}}} | [] | modbus
35 | 41 | DIF_COMPRESORES_CALOR | Diferencial Compresores Calor | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -99.9 | 99.9 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Dif.Heat compressors"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Diferencial Compresores Calor"}}} | [] | modbus
36 | 42 | DIF_COMPRESOR_RECUP_CALOR | Diferencial Compresor Recuperación Calor | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -99.9 | 99.9 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Dif.Heat recovery compressor"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Diferencial Compresor Recuperación Calor"}}} | [] | modbus
37 | 43 | DIF_COMPUERTA_FRIO | Diferencial Compuerta Frío | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -99.9 | 99.9 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Dif.Cool damper"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Diferencial Compuerta Frío"}}} | [] | modbus
38 | 44 | DIF_COMPRESORES_FRIO | Diferencial Compresores Frío | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -99.9 | 99.9 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Dif.Cool compressors"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Diferencial Compresores Frío"}}} | [] | modbus
39 | 45 | DIF_VALV_3_VIAS_APOYO_FRIO | Diferencial Válvula 3 Vías Apoyo Frio | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -99.9 | 99.9 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Dif.Cool 3WV"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Diferencial Válvula 3 Vías Apoyo Frio"}}} | [] | modbus
40 | 46 | DIF_COMPRESOR_RECUP_FRIO | Diferencial Compresor Recuperación Frío | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -99.9 | 99.9 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Dif.Cool recovery compressor"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Diferencial Compresor Recuperación Frío"}}} | [] | modbus
41 | 56 | Dif_Lim_Temp | Diferencial Limitadora Impulsión | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 99.9 | °C |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Differential limit temp"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Diferencial Limitadora Impulsión"}}} | [] | modbus
42 | 57 | Set_Lim_Temp_Baja | Consigna Limite de la Temperatura de baja en impulsión | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -99.9 | 99.9 | °C |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Setpoint limit of supply low temperature"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna Limite de la Temperatura de baja en impulsión"}}} | [] | modbus
43 | 58 | Set_Lim_Temp_Alta | Consigna Limite de la Temperatura de alta en impulsión | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 99.9 | °C |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Set point limit of supply high temperature"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna Limite de la Temperatura de alta en impulsión"}}} | [] | modbus
44 | 59 | CONSIGNA_INI_DESESCARC_PRESS | Consigna Inicio Desescarche por Presión | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 99.9 | % |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Defrost start"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna Inicio Desescarche por Presión"}}} | [] | modbus
45 | 60 | CONSIGNA_FORZ_DESESCARC_PRESS | Consigna Inicio Forzado Desescarche por Presión | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1000 | % |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Forced start"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna Inicio Forzado Desescarche por Presión"}}} | [] | modbus
46 | 61 | CONSIGNA_FIN_DESESCARC_PRESS | Consigna Fin Desescarche por Presión | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1000 | % |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Defrost end"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna Fin Desescarche por Presión"}}} | [] | modbus
47 | 62 | ZM_AUTO | Zona Muerta permanente cuando se trabaja en Modo Automatico | SERVICES |  | simple | 0 | 3 | 6 | -99.9 | 99.9 | °C |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Permanent Dead Zone when working in Automatic Mode"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Zona Muerta permanente cuando se trabaja en Modo Automatico"}}} | [] | modbus
48 | 63 | ZM_HUM | Zona Muerta Consigna Humedad | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 99.9 | % |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Setpoint dead zone humidity"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Zona Muerta Consigna Humedad"}}} | [] | modbus
49 | 64 | A6_SH_EVAP_TEMP | Temperatura Evaporación Válvula A | PARAMETERS |  | simple | 0 | 3 | 6 | -76 | 392 | °C/°F |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Evaporation temperature valve A"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura Evaporación Válvula A"}}} | [] | modbus
50 | 65 | ENTALPIA_RET | Entalpía Retorno | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 3276.7 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Return enthalphy"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Entalpía Retorno"}}} | [] | modbus
51 | 66 | A17_EEV_POSITION_PERCENT_SHOW | Porcentaje Apertura Válvula Circuito 1 | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 100 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Opening percent valve circuit 1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Porcentaje Apertura Válvula Circuito 1"}}} | [] | modbus
52 | 67 | TEMP_IMPULSION_2 | Temperatura Impulsión 2 | STATUS |  | basic | 60 | 4 | 0 | -3276.8 | 3276.7 | °C |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Supply temp. 2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura Impulsión 2"}}} | [] | modbus
53 | 68 | TempSetP_THTune_1 | Consigna Temperatura desde TH-Tune | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 100 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"From TH-TUNE Setpoint Confor"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna Temperatura desde TH-Tune"}}} | [] | modbus
54 | 69 | T_RET_AMB_VIR | Temperatura Retorno Ambiente | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -3276.8 | 3276.7 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Ambient/Return temperature"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura Retorno Ambiente"}}} | [] | modbus
55 | 70 | TEMP_EVAP_CIRC_1 | Temperatura Evaporador C1 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -3276.8 | 3276.7 | °C |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Evaporator temperature circuit 1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura Evaporador C1"}}} | [] | modbus
56 | 71 | DEMANDA_T_GLOBAL | Temperatura demandada cuando se trabaja en modo Global. (Mod | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 100 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Temperature demanded when working in Global mode (Global mod"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura demandada cuando se trabaja en modo Global. (Mod"}}} | [] | modbus
57 | 73 | TEMP_EVAP_CIRC_2 | Temperatura Evaporador C2 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -3276.8 | 3276.7 | °C |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Evaporator temperature circuit 2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura Evaporador C2"}}} | [] | modbus
58 | 74 | PB_1 | Presión Evaporador C1 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -3276.8 | 3276.7 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Evaporator pressure circuit 1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Presión Evaporador C1"}}} | [] | modbus
59 | 75 | T_PB_1 | Presion Evaporación Circuito 1 Convertida A Temperatura | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -3276.8 | 3276.7 | °C |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Evaporator pressure circuit 1 to temperature"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Presion Evaporación Circuito 1 Convertida A Temperatura"}}} | [] | modbus
60 | 76 | PB_2 | Presión Evaporador C2 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -3276.8 | 3276.7 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Evaporator pressure circuit 2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Presión Evaporador C2"}}} | [] | modbus
61 | 77 | T_PB_2 | Presion Evaporación Circuito 2 Convertida A Temperatura | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -3276.8 | 3276.7 | °C |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Evaporator pressure circuit 2 to temperature"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Presion Evaporación Circuito 2 Convertida A Temperatura"}}} | [] | modbus
62 | 78 | PB_3 | Presión Evaporador C3 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -3276.8 | 3276.7 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Evaporator pressure circuit 3"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Presión Evaporador C3"}}} | [] | modbus
63 | 80 | VENT_EXT_CIRC1_ANALOG | Control Ventilador Exterior Circuito 1 | ALARM |  | simple | 30 | 1 | 0 | 0 | 100 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Analog external fan circuit 1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Control Ventilador Exterior Circuito 1"}}} | [] | modbus
64 | 81 | VENT_EXT_CIRC2_ANALOG | Control Ventilador Exterior Circuito 2 | ALARM |  | simple | 30 | 1 | 0 | 0 | 100 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Analog external fan circuit 2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Control Ventilador Exterior Circuito 2"}}} | [] | modbus
65 | 82 | VENT_EXT_CIRC3_ANALOG | Control Ventilador Exterior Circuito 3 | ALARM |  | simple | 30 | 1 | 0 | 0 | 100 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Analog external fan circuit 3"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Control Ventilador Exterior Circuito 3"}}} | [] | modbus
66 | 83 | T_RET_AGUA | Temperatura Retorno Agua V3V | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -3276.8 | 3276.7 | °C |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Return water temp 3WV"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura Retorno Agua V3V"}}} | [] | modbus
67 | 84 | Current_1_L_SPV | Corriente Línea 1, empleo del opcional medidor de energía | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 999.9 | A |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Current Line 1, use of optional power meter"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Corriente Línea 1, empleo del opcional medidor de energía"}}} | [] | modbus
68 | 85 | Current_2_L_SPV | Corriente Línea 2, empleo del opcional medidor de energía | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 999.9 | A |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Current line 2, use of optional power meter"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Corriente Línea 2, empleo del opcional medidor de energía"}}} | [] | modbus
69 | 86 | Current_3_L_SPV | Corriente Línea 3, empleo del opcional medidor de energía | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 999.9 | A |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Current line 3, use of optional power meter"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Corriente Línea 3, empleo del opcional medidor de energía"}}} | [] | modbus
70 | 87 | Apparent_Power_1_L_SPV | Potencia Aparente 1, empleo del opcional medidor de energía | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 999.9 | kVAr |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Reactive power 1, use of optional power meter"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Potencia Aparente 1, empleo del opcional medidor de energía"}}} | [] | modbus
71 | 88 | Apparent_Power_2_L_SPV | Potencia Aparente 2, empleo del opcional medidor de energía | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 999.9 | kVAr |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Reactive power 2, use of optional power meter"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Potencia Aparente 2, empleo del opcional medidor de energía"}}} | [] | modbus
72 | 89 | Apparent_Power_3_L_SPV | Potencia Aparente 3, empleo del opcional medidor de energía | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 999.9 | kVAr |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Reactive power 3, use of optional power meter"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Potencia Aparente 3, empleo del opcional medidor de energía"}}} | [] | modbus
73 | 90 | Apparent_Power_L_SPV | Potencia Aparente Total, empleo del opcional medidor de ener | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 999.9 | kVA |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Apparent power, use of optional power meter"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Potencia Aparente Total, empleo del opcional medidor de ener"}}} | [] | modbus
74 | 91 | Reactive_Power_1_L_SPV | Potencia Reactiva 1, empleo del opcional medidor de energía | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 999.9 | kVAr |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Reactive power 1, use of optional power meter"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Potencia Reactiva 1, empleo del opcional medidor de energía"}}} | [] | modbus
75 | 92 | Reactive_Power_2_L_SPV | Potencia Reactiva 2, empleo del opcional medidor de energía | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 999.9 | kVAr |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Reactive power 2, use of optional power meter"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Potencia Reactiva 2, empleo del opcional medidor de energía"}}} | [] | modbus
76 | 94 | Reactive_Power_3_L_SPV | Potencia Reactiva 3, empleo del opcional medidor de energía | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 999.9 | kVAr |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Reactive power 3, use of optional power meter"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Potencia Reactiva 3, empleo del opcional medidor de energía"}}} | [] | modbus
77 | 95 | Reactive_Power_L_SPV | Potencia Reactiva Total, empleo del opcional medidor de ener | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 999.9 | kVAr |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Reactive power, use of optional power meter"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Potencia Reactiva Total, empleo del opcional medidor de ener"}}} | [] | modbus
78 | 96 | Power_1_L_SPV | Potencia Línea 1, empleo del opcional medidor de energía | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 999.9 | kW |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Power 1, use of optional power meter"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Potencia Línea 1, empleo del opcional medidor de energía"}}} | [] | modbus
79 | 97 | Power_2_L_SPV | Potencia Línea 2, empleo del opcional medidor de energía | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 999.9 | kW |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Power 2, use of optional power meter"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Potencia Línea 2, empleo del opcional medidor de energía"}}} | [] | modbus
80 | 98 | Power_3_L_SPV | Potencia Línea 3, empleo del opcional medidor de energía | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 999.9 | kW |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Power 3, use of optional power meter"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Potencia Línea 3, empleo del opcional medidor de energía"}}} | [] | modbus
81 | 100 | MAX_CURRENT | Corriente Máxima, empleo del opcional medidor de energía | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -5 | 3276.7 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Maximum current, use of optional power meter"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Corriente Máxima, empleo del opcional medidor de energía"}}} | [] | modbus
82 | 101 | CURRENT_DIFF | Diferencial Corriente, empleo del opcional medidor de energí | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 3276.7 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Current differential, use of optional power meter"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Diferencial Corriente, empleo del opcional medidor de energí"}}} | [] | modbus
83 | 102 | MAX_POWER | Potencia Máxima, empleo del opcional medidor de energía | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -5 | 3276.7 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Maximum power, use of optional power meter"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Potencia Máxima, empleo del opcional medidor de energía"}}} | [] | modbus
84 | 103 | POWER_DIFF | Diferencial Potencia, empleo del opcional medidor de energía | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 3276.7 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Power differential, use of optional power meter"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Diferencial Potencia, empleo del opcional medidor de energía"}}} | [] | modbus
85 | 104 | PRESS_COND_CIRC_1_CONV | Presión Condensador Circuito 1 Convertido A Temperatura | STATUS |  | basic | 60 | 4 | 0 | -3276.8 | 3276.7 | °C |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Condensator pressure circuit 1 to temperature"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Presión Condensador Circuito 1 Convertido A Temperatura"}}} | [] | modbus
86 | 105 | PRESS_COND_CIRC_2_CONV | Presión Condensador Circuito 2 Convertido A Temperatura | STATUS |  | basic | 60 | 4 | 0 | -3276.8 | 3276.7 | °C |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Condensator pressure circuit 2 to temperature"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Presión Condensador Circuito 2 Convertido A Temperatura"}}} | [] | modbus
87 | 107 | PRESS_COND_CIRC_REC_CONV | Presión Condensador Circuito Recuperación Convertida A Tempe | STATUS |  | basic | 60 | 4 | 0 | -3276.8 | 3276.7 | °C |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Condensator pressure recovery circuit to temperature"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Presión Condensador Circuito Recuperación Convertida A Tempe"}}} | [] | modbus
88 | 108 | CONSIGNA_TRABAJO | Consigna Trabajo se le asignará un valor u otro en función d | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -3276.8 | 3276.7 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Working Setpoint will be assigned one value or another depen"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna Trabajo se le asignará un valor u otro en función d"}}} | [] | modbus
89 | 110 | Min_Mix_Damper | Apertura Mínima Compuerta Mezcla | DAMPERS |  | simple | 0 | 3 | 6 | 0 | 100 | % |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Minimum opening for mixing damper"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Apertura Mínima Compuerta Mezcla"}}} | [] | modbus
90 | 111 | SET_PRESS_COND_CIRC1 | Consigna Presión Condensación del Circuito | SERVICES |  | simple | 0 | 3 | 6 | 0 | 3276.7 | BAR |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Condensation circuit pressure setpoint"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna Presión Condensación del Circuito"}}} | [] | modbus
91 | 112 | DIF_PRESS_COND_CIRC1 | Diferencial Presión Condensación del Circuito | SERVICES |  | simple | 0 | 3 | 6 | 0 | 99.9 | BAR |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Condensation circuit pressure differential"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Diferencial Presión Condensación del Circuito"}}} | [] | modbus
92 | 113 | SET_PRESS_EVAP_CIRC1 | Consigna Presión Evaporación del Circuito | SERVICES |  | simple | 0 | 3 | 6 | 0 | 3276.7 | BAR |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Evaporation circuit pressure circuit setpoint"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna Presión Evaporación del Circuito"}}} | [] | modbus
93 | 114 | DIF_PRESS_EVAP_CIRC1 | Diferencial Presión Evaporación del Circuito | SERVICES |  | simple | 0 | 3 | 6 | 0 | 99.9 | BAR |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Evaporation circuit pressure circuit differential"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Diferencial Presión Evaporación del Circuito"}}} | [] | modbus
94 | 115 | Recuc_Power_Req_1 | Reducido por Alta Presión Condensación | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -3276.8 | 3276.7 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Reduced power request 1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Reducido por Alta Presión Condensación"}}} | [] | modbus
95 | 116 | Reduc_Power_Req_2 | Reducido por Alta Presión Condensación | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -3276.8 | 3276.7 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Reduced power request 2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Reducido por Alta Presión Condensación"}}} | [] | modbus
96 | 117 | DEM_CAUDAL | Porcentaje de Caudal de Aire Solicitado | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -3276.8 | 3276.7 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Percentage of Air Flow Requested"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Porcentaje de Caudal de Aire Solicitado"}}} | [] | modbus
97 | 118 | DEM_CAUDAL_BMS | Porcentaje de Caudal de aire solicitado por BMS | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1000 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Percentage of air flow requested by BMS"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Porcentaje de Caudal de aire solicitado por BMS"}}} | [] | modbus
98 | 119 | TEMP_RET_AMB_0 | Temperatura Retorno / Ambiente para placa de rotación | STATUS |  | basic | 60 | 4 | 0 | -3276.7 | 3276.7 | °C |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Return / Ambient temperature for rotating plate"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura Retorno / Ambiente para placa de rotación"}}} | [] | modbus
99 | 120 | Posicion_VEE_1 | Porcentaje Apertura VEE Circuito 1 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -3276.8 | 3276.7 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Opening percent VEE circuit 1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Porcentaje Apertura VEE Circuito 1"}}} | [] | modbus
100 | 121 | Superheat_Circ1 | Sobrecalentamiento Circuito 1 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -72 | 324 | °C/°F |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Superheat circuit 1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Sobrecalentamiento Circuito 1"}}} | [] | modbus
101 | 122 | Suction_Temp_Circ1 | Temperatura Aspiracion VEE Circuito 1 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -3276.8 | 3276.7 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Suction temperature VEE circuit 1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura Aspiracion VEE Circuito 1"}}} | [] | modbus
102 | 123 | Evap_Press_Circ1 | Presion Evaporador VEE Circuito 1 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -3276.8 | 3276.7 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Evaporator pressure VEE circuit 1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Presion Evaporador VEE Circuito 1"}}} | [] | modbus
103 | 124 | Evaporation_Temp_Circ1 | Temperatura Equivalente Evaporacion VEE Circuito 1 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -3276.8 | 3276.7 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Evaporation temperature VEE circuit 1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura Equivalente Evaporacion VEE Circuito 1"}}} | [] | modbus
104 | 125 | Posicion_VEE_2 | Porcentaje Apertura VEE Circuito 2 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -3276.8 | 3276.7 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Opening percent VEE circuit 2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Porcentaje Apertura VEE Circuito 2"}}} | [] | modbus
105 | 126 | Superheat_Circ2 | Sobrecalentamiento Circuito 2 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -72 | 324 | °C/°F |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Superheating circuit 2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Sobrecalentamiento Circuito 2"}}} | [] | modbus
106 | 127 | Suction_Temp_Circ2 | Temperatura Aspiracion VEE Circuito 2 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -3276.8 | 3276.7 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Suction temperature VEE circuit 2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura Aspiracion VEE Circuito 2"}}} | [] | modbus
107 | 128 | Evap_Press_Circ2 | Presion Evaporador VEE Circuito 2 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -3276.8 | 3276.7 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Evaporator pressure VEE circuit 2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Presion Evaporador VEE Circuito 2"}}} | [] | modbus
108 | 129 | Evaporation_Temp_Circ2 | Temperatura Equivalente Evaporacion VEE Circuito 2 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -3276.8 | 3276.7 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Evaporation temperature VEE circuit 2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura Equivalente Evaporacion VEE Circuito 2"}}} | [] | modbus
109 | 130 | TEMP_RETORNO | Temperatura Retorno Aire (Medidor de Energía Térmica) | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -3276.8 | 3276.7 | °C |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Air Return Temperature (Thermal Energy Meter)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura Retorno Aire (Medidor de Energía Térmica)"}}} | [] | modbus
110 | 131 | HUM_RETORNO | Humedad Retorno Aire (Medidor de Energia Térmica) | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -3276.8 | 3276.7 | °C |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Return Air Humidity (Thermal Energy Meter)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Humedad Retorno Aire (Medidor de Energia Térmica)"}}} | [] | modbus
111 | 132 | CorrienteVImpulsion | Corriente Ventilador Impulsión | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 3276.7 | A |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Supply fan current"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Corriente Ventilador Impulsión"}}} | [] | modbus
112 | 133 | CorrienteVRetorno | Corriente Ventilador Retorno | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 3276.7 | A |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Return fan current"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Corriente Ventilador Retorno"}}} | [] | modbus
113 | 134 | EDV_1.A7_SH_EVAP_PRES_msk | Presion de Evaporación Circuito 1 proveniente de driver | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -290 | 2900 | barg/psig |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Evaporating Pressure Circuit 1 coming from driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Presion de Evaporación Circuito 1 proveniente de driver"}}} | [] | modbus
114 | 135 | EDV_1.A6_SH_EVAP_TEMP_msk | Temperatura evaporación Circuito 2 proveniente de driver | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -76 | 392 | °C/°F |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Evaporating temperature Circuit 2 from driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura evaporación Circuito 2 proveniente de driver"}}} | [] | modbus
115 | 136 | EDV_1.A68_SH_SH_2ND_msk | Recalentamiento de circuito 2 proveniente de driver | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -72 | 324 | K/°F |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Circuit 2 overheating coming from driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Recalentamiento de circuito 2 proveniente de driver"}}} | [] | modbus
116 | 137 | EDV_1.A69_SH_SUCT_TEMP_2ND_msk | Temperatura de aspiración del circuito 2 proveniente de driv | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -76 | 392 | °C/°F |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Suction temperature of circuit 2 coming from driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura de aspiración del circuito 2 proveniente de driv"}}} | [] | modbus
117 | 138 | DEMANDA_RESISTENCIAS | Demandad Quemador de Gas/Resistencias | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 100 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Gas Burner Demand/Resistances"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Demandad Quemador de Gas/Resistencias"}}} | [] | modbus
118 | 139 | Reduc_Power_Req_Recup | Dada la demanda del Compresor de Recuperación se calcula con | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -3276.8 | 3276.7 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Given the demand of the recovery compressor, the required de"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Dada la demanda del Compresor de Recuperación se calcula con"}}} | [] | modbus
119 | 140 | HUMIDIFICADOR_ANALOG | Valor Control Humidificador | ALARM |  | simple | 30 | 1 | 0 | 0 | 100 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Analog humidifier"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Valor Control Humidificador"}}} | [] | modbus
120 | 141 | TEMP_QUEDOR_GAS | Temperatura Quemador Gas | STATUS |  | basic | 60 | 4 | 0 | -3276.8 | 3276.7 | °C |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Gas-burner temp"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura Quemador Gas"}}} | [] | modbus
121 | 142 | P_EVAP_CR | Presión Evaporación Circuito Recuperación | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -3276.8 | 3276.7 | BAR |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Evaporation pressure recovery circuit"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Presión Evaporación Circuito Recuperación"}}} | [] | modbus
122 | 143 | ENTALPIA_INT | Entalpía Interior | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 3276.7 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Ambient entha."},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Entalpía Interior"}}} | [] | modbus
123 | 144 | ENTALPIA_EXT | Entalpía Exterior | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 3276.7 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Outdoor entha."},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Entalpía Exterior"}}} | [] | modbus
124 | 145 | CONSIGNA_ENTALPIA | Consigna Entalpía | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 3276.7 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Enthalphy set."},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna Entalpía"}}} | [] | modbus
125 | 146 | ENTALPIA_POST | Entalpía Post Batería | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 3276.7 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Postbat. Entha"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Entalpía Post Batería"}}} | [] | modbus
126 | 147 | TemperVImpulsion | Temperatura Ventilador Impulsión | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 3276.7 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Supply fan temperature"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura Ventilador Impulsión"}}} | [] | modbus
127 | 148 | TemperVRetorno | Temperatura Ventilador Retorno | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 3276.7 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Return fan temperature"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura Ventilador Retorno"}}} | [] | modbus
128 | 149 | VALV_3_VIAS_APOYO | Válvula 3 Vías Apoyo | ALARM |  | simple | 30 | 1 | 0 | 0 | 100 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"3WV demand"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Válvula 3 Vías Apoyo"}}} | [] | modbus
129 | 151 | EDV_1.A66_EEV_POS_PERCENT_2ND_SHOW | Porcentaje Apertura Válvula Circuito 2 proveniente de driver | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 100 | % |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Valve Opening Percentage Circuit 2 from driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Porcentaje Apertura Válvula Circuito 2 proveniente de driver"}}} | [] | modbus
130 | 152 | EDV_1.A70_SH_EVAP_TEMP_2ND_msk | Temperatura evaporación Circuito 2 proveniente de driver | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -76 | 392 | °C/°F |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Evaporation temperature of circuit 2 coming from driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura evaporación Circuito 2 proveniente de driver"}}} | [] | modbus
131 | 153 | EDV_1.A71_SH_EVAP_PRES_2ND_msk | Presión Evaporación del circuito 2 proveniente de driver | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -290 | 2900 | barg/psig |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Pressure Evaporation of circuit 2 from driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Presión Evaporación del circuito 2 proveniente de driver"}}} | [] | modbus
132 | 154 | EDV_1.A10_SH_SH_msk | Recalentamiento del circuito 1 proveniente proveniente de dr | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -72 | 324 | K/°F |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Superheating of circuit 1 from driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Recalentamiento del circuito 1 proveniente proveniente de dr"}}} | [] | modbus
133 | 155 | EDV_1.A5_SH_SUCT_TEMP_msk | Temperatura Aspiración Válvula circuito 1 proveniente de dri | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -76 | 392 | °C/°F |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Suction temperature Valve circuit 1 from driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura Aspiración Válvula circuito 1 proveniente de dri"}}} | [] | modbus
134 | 156 | A17_EEV_POSITION_PERCENT_SHOW_2 | Porcentaje Apertura Válvula Circuito 1 proveniente de placa | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 100 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Valve Opening Percentage Circuit 1 from the board"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Porcentaje Apertura Válvula Circuito 1 proveniente de placa"}}} | [] | modbus
135 | 157 | EDV_2.A7_SH_EVAP_PRES_msk | Presión Evaporación Válvula circuito 1 proveniente de driver | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -290 | 2900 | barg/psig |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Evaporating pressure Evaporating pressure Valve circuit 1 fr"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Presión Evaporación Válvula circuito 1 proveniente de driver"}}} | [] | modbus
136 | 158 | EDV_2.A6_SH_EVAP_TEMP_msk | Temperatura Evaporación circuito 1 proveniente de driver | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -76 | 392 | °C/°F |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Evaporating temperature of circuit 1 from driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura Evaporación circuito 1 proveniente de driver"}}} | [] | modbus
137 | 159 | A10_SH_SH | Recalentamiento del circuito 1 proveniente de placa | PARAMETERS |  | simple | 0 | 4 | 0 | -72 | 324 | °C/°F |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Overheating of circuit 1 coming from the board"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Recalentamiento del circuito 1 proveniente de placa"}}} | [] | modbus
138 | 160 | A5_SH_SUCT_TEMP | Temperatura Aspiración circuito 1 proveniente de placa | PARAMETERS |  | simple | 0 | 4 | 0 | -76 | 392 | °C/°F |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Suction temperature circuit 1 coming from the board"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura Aspiración circuito 1 proveniente de placa"}}} | [] | modbus
139 | 162 | A7_SH_EVAP_PRES | Presión Evaporación circuito 1 proveniente de placa | PARAMETERS |  | simple | 0 | 4 | 0 | -290 | 2900 | barg |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Evaporation pressure circuit 1 coming from the board"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Presión Evaporación circuito 1 proveniente de placa"}}} | [] | modbus
140 | 163 | EDV_1.A68_SH_SH_2ND | Recalentamiento circuito 2 proveniente de placa | PARAMETERS |  | simple | 0 | 4 | 0 | -72 | 324 | °C/°F |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Superheat circuit 2 coming from the board"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Recalentamiento circuito 2 proveniente de placa"}}} | [] | modbus
141 | 164 | EDV_1.A69_SH_SUCT_TEMP_2ND | Temperatura Aspiración circuio 2 proveniente de placa | PARAMETERS |  | simple | 0 | 4 | 0 | -76 | 392 | °C/°F |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Suction temperature circuit 2 coming from the board"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura Aspiración circuio 2 proveniente de placa"}}} | [] | modbus
142 | 166 | A71_SH_EVAP_PRES_2ND | Presión Evaporación circuito 2 proveniente de placa | PARAMETERS |  | simple | 0 | 4 | 0 | -290 | 2900 | barg |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Evaporation pressure circuit 2 coming from the board"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Presión Evaporación circuito 2 proveniente de placa"}}} | [] | modbus
143 | 167 | A70_SH_EVAP_TEMP_2ND | Temperatura Evaporación circuito 2 proveniente de placa | PARAMETERS |  | simple | 0 | 3 | 6 | -76 | 392 | °C/°F |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Evaporation temperature circuit 2 coming from the board"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura Evaporación circuito 2 proveniente de placa"}}} | [] | modbus
144 | 168 | P_EVAP_CR_CONV | Temperatura de condensación del circuito de Recuperación, p | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -3276.8 | 3276.7 | °C |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Condensing temperature of the recovery circuit, pressure con"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura de condensación del circuito de Recuperación, p"}}} | [] | modbus
145 | 170 | EDV_1.A5_SH_SUCT_TEMP_msk_2 | Temperatura Aspiración Circuito 1 proveniente del driver | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -76 | 392 | °C/°F |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Suction temperature circuit 1 coming from driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura Aspiración Circuito 1 proveniente del driver"}}} | [] | modbus
146 | 171 | T_DESC_C1 | Temperatura Descarga Circuito 1 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -3276.8 | 3276.7 | °C |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Discharge temperature circuit 1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura Descarga Circuito 1"}}} | [] | modbus
147 | 172 | T_DESC_C2 | Temperatura Descarga Circuito 2 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -3276.8 | 3276.7 | °C |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Discharge temperature circuit 2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura Descarga Circuito 2"}}} | [] | modbus
148 | 174 | T_DESC_CR | Temperatura Descarga Circuito Recuperacion | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -3276.8 | 3276.7 | °C |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Discharge temperature recovery circuit"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura Descarga Circuito Recuperacion"}}} | [] | modbus
149 | 175 | ENTALPIA_IMP | Entalpía Impulsión | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 3276.7 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Supply enthalphy"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Entalpía Impulsión"}}} | [] | modbus
150 | 180 | EDV_2.A68_SH_SH_2ND_msk | Recalentamiento del circuito 4 proveniente de driver | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -72 | 324 | K/°F |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Superheat - circuit 4 from driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Recalentamiento del circuito 4 proveniente de driver"}}} | [] | modbus
151 | 185 | MotTemp | Temperatura Devanado Motor del Ventilador | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -999.9 | 999.9 | °C |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Fan motor winding temperature"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura Devanado Motor del Ventilador"}}} | [] | modbus
152 | 186 | CONSIGNA_AUTO_ECO | Consigna Modo Auto, Cuando activamos consigna eco 2 | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -99.9 | 99.9 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Auto mode setpoint, when we activate eco 2 setpoint"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna Modo Auto, Cuando activamos consigna eco 2"}}} | [] | modbus
153 | 187 | DIF_RESIS_DES_PERM | Diferencial Resistencia Deshumectación Permanente Pantalla B | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 99.9 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Permanent Dehumidification Resistance Differential. Screen B"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Diferencial Resistencia Deshumectación Permanente Pantalla B"}}} | [] | modbus
154 | 188 | Freq_L_SPV | Frecuencia en Medido de Energía | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 999.9 | Hz |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Frequency in Energy Measurement"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Frecuencia en Medido de Energía"}}} | [] | modbus
155 | 189 | TEMP_EXT_PROTEC_COMPRE | Temperatura Protección Compresores Exterior. Pantalla Ha19 | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -3276.8 | 3276.7 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Lock operating compressors by external temp. Screen Ha19"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura Protección Compresores Exterior. Pantalla Ha19"}}} | [] | modbus
156 | 190 | DIF_TEMP_EXT_PROTEC_COMPRE | Diferencial Temperatura Protección Compresores Exterior. Pa | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -3276.8 | 3276.7 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Lock operating compressors by external temp differential. Sc"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Diferencial Temperatura Protección Compresores Exterior. Pa"}}} | [] | modbus
157 | 191 | TEMP_EXT_REDUC_COMPRE | Temperatura Exterior Reduce nº Compresores. Ha19 | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -3276.8 | 3276.7 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Compressors reduction by external temp. Ha19"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura Exterior Reduce nº Compresores. Ha19"}}} | [] | modbus
158 | 192 | TEMP_EXT_FIN_REDUC_COMPRE | Temperatura Exterior Finaliza la Reduccion nº Compresores. H | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -3276.8 | 3276.7 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Compressors reduction end by external temp. Ha19"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura Exterior Finaliza la Reduccion nº Compresores. H"}}} | [] | modbus
159 | 193 | CONSIGNA_RESIST_PRE | Consigna Resistencia Precalentamiento. Ha28 | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -3276.8 | 3276.7 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Preheating resistance setpoint. Ha28"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna Resistencia Precalentamiento. Ha28"}}} | [] | modbus
160 | 194 | DIF_RESIST_PRE | Diferencial Resistencia Precalentamiento. Ha28 | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -3276.8 | 3276.7 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Preheating resistance differential. Ha28"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Diferencial Resistencia Precalentamiento. Ha28"}}} | [] | modbus
161 | 195 | FullInv_ZM_C1 | Zona Muerta 1 Calor | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 100 | °C/°F |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Heat dead zone 1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Zona Muerta 1 Calor"}}} | [] | modbus
162 | 196 | FullInv_Dif_C1 | Diferencial 1 Calor | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 100 | °C/°F |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Heat differential 1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Diferencial 1 Calor"}}} | [] | modbus
163 | 197 | FullInv_ZM_C2 | Zona Muerta 2 Calor | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 100 | °C/°F |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Heat dead zone 2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Zona Muerta 2 Calor"}}} | [] | modbus
164 | 198 | FullInv_Dif_C2 | Diferencial 2 Calor | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 100 | °C/°F |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Heat differential 2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Diferencial 2 Calor"}}} | [] | modbus
165 | 199 | FullInv_ZM_F1 | Zona Muerta 1 Frío | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 100 | °C/°F |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Cool dead zone 1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Zona Muerta 1 Frío"}}} | [] | modbus
166 | 200 | FullInv_Dif_F1 | Diferencial 1 Frío | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 100 | °C/°F |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Cool differential 1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Diferencial 1 Frío"}}} | [] | modbus
167 | 201 | FullInv_ZM_F2 | Zona Muerta 2 Frío | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 100 | °C/°F |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Cool dead zone 2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Zona Muerta 2 Frío"}}} | [] | modbus
168 | 202 | FullInv_Dif_F2 | Diferencial 2 Frío | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 100 | °C/°F |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Cool differential 2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Diferencial 2 Frío"}}} | [] | modbus
169 | 244 | SP_PresVentilador | Ventilador Interior EBM. Valor mínimo de presión ventilación | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 3276.7 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Indoor EBM fan.Ventilation minimun pressure"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Ventilador Interior EBM. Valor mínimo de presión ventilación"}}} | [] | modbus
170 | 245 | Dif_PresVentilador | Diferencial de suministro de baja presión en ventiladores in | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 3276.7 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Low pressure supply differential on indoor fans EBM"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Diferencial de suministro de baja presión en ventiladores in"}}} | [] | modbus
171 | 246 | DEM_CAUDAL_MIN_VENT | Límite mínimo demanda de velocidad Caudal Ventiladores | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 100 | % |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Minimum speed demand limit Flow rate Fans"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Límite mínimo demanda de velocidad Caudal Ventiladores"}}} | [] | modbus
172 | 247 | DEM_CAUDAL_MAX_VENT | Límite máximo demanda de velocidad Caudal Ventiladores | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 100 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Maximum speed demand limit Flow rate Fans"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Límite máximo demanda de velocidad Caudal Ventiladores"}}} | [] | modbus
173 | 248 | DEM_CAUDAL_OFF_COMPRE | Seguridad Compresores, % mínimo caudal de aire impulsado par | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 100 | % |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Compressor safety, % minimum driven air flow for compressor "},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Seguridad Compresores, % mínimo caudal de aire impulsado par"}}} | [] | modbus
174 | 249 | DEM_CAUDAL_ON_COMPRE | Seguridad Compresores, % caudal de aire impulsado para arran | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 100 | % |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Compressor safety, % compressor start-up air flow rate. Hc21"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Seguridad Compresores, % caudal de aire impulsado para arran"}}} | [] | modbus
175 | 250 | Dif_Demanda_Lim | Diferencial demanda Límite de compresores en función del cau | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 99.9 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Differential demand Compressor limit as a function of driven"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Diferencial demanda Límite de compresores en función del cau"}}} | [] | modbus
176 | 251 | OffsetDemCaudal | Se emplea en Cálculo de la demanda de compresores en función | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -3276.8 | 3276.7 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"It is used in the calculation of compressor demand as a func"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Se emplea en Cálculo de la demanda de compresores en función"}}} | [] | modbus
177 | 272 | EDV_2.A34_S1_VALUE_OFFSET_msk | Valor del diferencial de la sonda 1 proveniente de driver | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -870 | 870 | barg/psig |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"value of probe 1 coming from driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Valor del diferencial de la sonda 1 proveniente de driver"}}} | [] | modbus
178 | 273 | EDV_2.A1_S1_VALUE_msk | Valor de la sonda 1 proveniente de driver | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -290 | 2900 | barg/psig |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"probe 1 offset value from driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Valor de la sonda 1 proveniente de driver"}}} | [] | modbus
179 | 274 | EDV_2.A41_S2_VALUE_OFFSET_msk | Valor del diferenical de la sonda 1 proveniente de driver | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -36 | 36 | °C/°F |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"probe 2 offset value from driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Valor del diferenical de la sonda 1 proveniente de driver"}}} | [] | modbus
180 | 275 | EDV_2.A2_S2_VALUE_msk | Valor de la sonda 2 proveniente de driver | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -870 | 2900 | °C/°F |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"value of probe 1 coming from driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Valor de la sonda 2 proveniente de driver"}}} | [] | modbus
181 | 276 | EDV_2.A35_S3_VALUE_OFFSET_msk | Valor diferencial sonda 3 proveniente de driver | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -870 | 870 | barg/psig |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"probe 3 offset value from driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Valor diferencial sonda 3 proveniente de driver"}}} | [] | modbus
182 | 277 | EDV_2.A3_S3_VALUE_msk | Valor sonda 3 proveniente de driver | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -290 | 2900 | barg/psig |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"value of probe 3 coming from driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Valor sonda 3 proveniente de driver"}}} | [] | modbus
183 | 278 | EDV_2.A42_S4_VALUE_OFFSET_msk | Valor diferencial sonda 4 proveniente driver | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -36 | 36 | °C/°F |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"probe 4 offset value from driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Valor diferencial sonda 4 proveniente driver"}}} | [] | modbus
184 | 279 | EDV_2. A4_S4_VALUE_msk | Valor Sonda 4 proveniente de driver | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -76 | 392 | °C/°F |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"value of probe 4 coming from driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Valor Sonda 4 proveniente de driver"}}} | [] | modbus
185 | 281 | A1_S1_VALUE | Valor Sonda 1. Menú Calibarción sondas | PARAMETERS |  | simple | 0 | 3 | 6 | -290 | 2900 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"S1 probe value. Probe calibration menu"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Valor Sonda 1. Menú Calibarción sondas"}}} | [] | modbus
186 | 283 | A2_S2_VALUE | Valor Sonda 2. Menú Calibarción sondas | PARAMETERS |  | simple | 0 | 3 | 6 | -870 | 2900 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"S2 Probe value. Probe calibration menu"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Valor Sonda 2. Menú Calibarción sondas"}}} | [] | modbus
187 | 285 | A3_S3_VALUE | Valor Sonda 3. Menú Calibarción sondas | PARAMETERS |  | simple | 0 | 3 | 6 | -290 | 2900 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"S3 probe value. Probe calibration menu"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Valor Sonda 3. Menú Calibarción sondas"}}} | [] | modbus
188 | 287 | A4_S4_VALUE | Valor Sonda 4. Menú Calibarción sondas | PARAMETERS |  | simple | 0 | 3 | 6 | -76 | 392 | °C/°F |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"S4 probe value. Probe calibration menu"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Valor Sonda 4. Menú Calibarción sondas"}}} | [] | modbus
189 | 288 | CONSIGNA_CALOR | Consigna Temperatura en función del Modo de funcionamiento V | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -99.9 | 99.9 | ºC |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Temperature set point as a function of operating mode Summer"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna Temperatura en función del Modo de funcionamiento V"}}} | [] | modbus
190 | 289 | Set_Lim_Hum_Alta | Consigna limitadora máxima Humedad Impulsión. Cuando la sond | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 99.9 | °C |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Maximum limiting set point for supply humidity. When the sup"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna limitadora máxima Humedad Impulsión. Cuando la sond"}}} | [] | modbus
191 | 290 | Dif_Lim_Hum | Diferencial de la limitadora máxima Humedad Impulsión. Cuand | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 99.9 | °C |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Maximum limiting differential for supply humidity. When the "},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Diferencial de la limitadora máxima Humedad Impulsión. Cuand"}}} | [] | modbus
192 | 291 | DIFERENCIAL_LIMITE_SECAR | Diferencial para generar una consigna limite de secado al pa | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -3276.8 | 3276.7 | °C |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Differential to generate a drying set point limit when going"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Diferencial para generar una consigna limite de secado al pa"}}} | [] | modbus
193 | 292 | CONSIGNA_LIMITE_SECAR | Consigna Limite Permiso Deshumectar. Gec10 | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -3276.8 | 3276.7 | °C |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Limit dry setpoint. Gec10"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna Limite Permiso Deshumectar. Gec10"}}} | [] | modbus
194 | 293 | DIF_COMP_MEZCLA | Diferencial Compuerta Mezcla | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 100 | °C |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Mixing damper differential"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Diferencial Compuerta Mezcla"}}} | [] | modbus
195 | 294 | HP_Al_Threshold | Consigna Alarma Presión en Alta | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1000 | % |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"High pressure alarm threshold"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna \tAlarma Presión en Alta"}}} | [] | modbus
196 | 295 | HP_Al_Hysteresis | Diferencial Alarma Presión en Alta | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 99.9 | % |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Dif. high pressure alarm"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Diferencial Alarma Presión en Alta"}}} | [] | modbus
197 | 296 | LP_Al_Threshold | Consigna Alarma Presión en Baja | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1000 | % |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Low pressure alarm threshold"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna \tAlarma Presión en Baja"}}} | [] | modbus
198 | 297 | LP_Al_Hysteresis | Diferencial Alarma Presión en Baja | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1000 | % |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Low pressure alarm differential"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Diferencial Alarma Presión en Baja"}}} | [] | modbus
199 | 298 | CUT_OFF_DIF_COND_CIRC1 | Diferencial de corte ventilador exterior Circuito 1 | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 99.9 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"External fan cut-off differential Circuit 1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Diferencial de corte ventilador exterior Circuito 1"}}} | [] | modbus
200 | 299 | MIN_SPEED_VENT_COND_CIRC1 | Mínima Velocidad Ventilador exterior Circuito 1 | SERVICES |  | simple | 0 | 3 | 6 | 0 | 100 | % |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Minimum Speed Outdoor fan Circuit 1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Mínima Velocidad Ventilador exterior Circuito 1"}}} | [] | modbus
201 | 300 | MAX_SPEED_VENT_COND_CIRC1 | Máxima Velocidad Ventilador exterior Circuito 1 | SERVICES |  | simple | 0 | 3 | 6 | 0 | 100 | % |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Minimum Speed Outdoor fan Circuit 1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Máxima Velocidad Ventilador exterior Circuito 1"}}} | [] | modbus
202 | 301 | Max_Ext_Damper | Máxima Apertura Compuerta Exterior | DAMPERS |  | simple | 0 | 3 | 6 | 0 | 100 | % |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Maximum Outer Damper Opening"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Máxima Apertura Compuerta Exterior"}}} | [] | modbus
203 | 302 | Max_Mix_Damper | Máxima Apertura Compuerta Mezcla | DAMPERS |  | simple | 0 | 3 | 6 | 0 | 100 | % |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Maximum opening for mixing damper"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Máxima Apertura Compuerta Mezcla"}}} | [] | modbus
204 | 303 | Set_External_Hum_Inf | Renovación Compuertas. Límite mínimo de humedad exterior. Ge | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -999.9 | 999.9 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Renovation Dampers. Minimum exterior humidity limit. Gec20"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Renovación Compuertas. Límite mínimo de humedad exterior. Ge"}}} | [] | modbus
205 | 304 | Set_External_Hum_Sup | Renovación Compuertas. Límite máximo de humedad exterior. Ge | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -999.9 | 999.9 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Renovation Dampers. Maximum exterior humidity limit. Gec20"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Renovación Compuertas. Límite máximo de humedad exterior. Ge"}}} | [] | modbus
206 | 305 | Dif_External_Hum | Diferencial Humedad Exterior en Renovación de compuertas por | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -999.9 | 999.9 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Outdoor Humidity Differential in renovation dampers by outdo"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Diferencial Humedad Exterior en Renovación de compuertas por"}}} | [] | modbus
207 | 306 | TEMP_MEZCLA_CONFORT_VER | Renovación compuertas. Límites de temperatura de mezcla en m | CONFIGURATION |  | simple | 0 | 3 | 6 | -99.9 | 99.9 | °C |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Renovation Dampers. Mixing temperature limits in summer mode"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Renovación compuertas. Límites de temperatura de mezcla en m"}}} | [] | modbus
208 | 307 | TEMP_MEZCLA_CONFORT_INV | Renovación compuertas. Límites de temperatura de mezcla en m | CONFIGURATION |  | simple | 0 | 3 | 6 | -99.9 | 99.9 | °C |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Renovation Dampers. Mixing temperature limits in winter mode"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Renovación compuertas. Límites de temperatura de mezcla en m"}}} | [] | modbus
209 | 308 | DIF_TEMP_MEZCLA_CONFORT | Diferencial de limite de temperatura de mezcla. Gec21 | CONFIGURATION |  | simple | 0 | 3 | 6 | -99.9 | 99.9 | °C |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Mixing temperature limit differential.\n Gec21"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Diferencial de limite de temperatura de mezcla. Gec21"}}} | [] | modbus
210 | 309 | CONS_T_MEZCLA_PROT | Consigna Temperatura Mezcla Renovación Compuertas Zona Neutr | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -999.9 | 999.9 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Regulation of set point (middle point of neutral zone)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna Temperatura Mezcla Renovación Compuertas Zona Neutr"}}} | [] | modbus
211 | 310 | DIF_TEMP_MEZCLA_PROT | Diferencial Temperatura Mezcla Renovación Compuertas Zona Ne | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0.1 | 999.9 | °C |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Regulation of differential in neutral zone"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Diferencial Temperatura Mezcla Renovación Compuertas Zona Ne"}}} | [] | modbus
212 | 311 | Diff_Reg_Incr_TMix | Diferencial de activación de zona neutra en renovación compu | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0.1 | 999.9 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Neutral zone activation differential in damper renovation du"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Diferencial de activación de zona neutra en renovación compu"}}} | [] | modbus
213 | 312 | Diff_Reg_Decr_TMix | Diferencial de desactivación de zona neutra en renovación co | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0.1 | 999.9 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Neutral zone deactivation differential in damper renewal due"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Diferencial de desactivación de zona neutra en renovación co"}}} | [] | modbus
214 | 313 | CONSIGNA_INI_DESESCARC_DELTA | Consigna Inicio Desescarche | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 99.9 | °C |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Defrost start setpoint"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna Inicio Desescarche"}}} | [] | modbus
215 | 314 | TempSetP_Min_THTune_1 | Consigna Temperatura Mínima por TH-TUNE | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -3276.7 | 3276.7 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Lower limit of the temperature setpoint value by TH-TUNE"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna Temperatura Mínima por TH-TUNE"}}} | [] | modbus
216 | 315 | TempSetP_Max_THTune_1 | Consigna Temperatura Máxima por TH-TUNE | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -3276.7 | 3276.7 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Upper limit of temperature setpoint value by TH-TUNE"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna Temperatura Máxima por TH-TUNE"}}} | [] | modbus
217 | 316 | A50_SH_SET_msk | Consigna recalentamiento circuito 1 en driver | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -72 | 324 | K/°C |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Setpoint superheat - circuit 1 in driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna recalentamiento circuito 1 en driver"}}} | [] | modbus
218 | 317 | A56_LOW_SH_THRESHOLD_msk | Umbral Mínimo recalentamiento circuito 1 en driver | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -72 | 324 | °K/°F |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Threshold Minimum Overheating - circuit 1 in driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Umbral Mínimo recalentamiento circuito 1 en driver"}}} | [] | modbus
219 | 318 | A52_LOP_THRESHOLD_msk | Umbral Mínimo Temperatura Evaporación circuito 1 en driver | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -76 | 3276.7 | °C/°F |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Threshold for low temperature of evaporation - circuit 1 in "},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Umbral Mínimo Temperatura Evaporación circuito 1 en driver"}}} | [] | modbus
220 | 319 | A54_MOP_THRESHOLD_msk | Umbral Máximo Temperatura Evaporación circuito 1 en driver | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -3276.8 | 392 | °C/°F |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Thresold high temperature evaporation - circuit 1 in driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Umbral Máximo Temperatura Evaporación circuito 1 en driver"}}} | [] | modbus
221 | 320 | A83_SH_SET_2ND_msk | Consigna recalentamiento circuito 2 en Driver | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -72 | 324 | K/°C |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Setpoint superheat cicuit 2 in driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna recalentamiento circuito 2 en Driver"}}} | [] | modbus
222 | 321 | A89_LOW_SH_THRESHOLD_2ND_msk | Umbral Mínimo recalentamiento circuito 2 en driver | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -72 | 324 | K/°C |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Low superheat thresold cicuit 2 in driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Umbral Mínimo recalentamiento circuito 2 en driver"}}} | [] | modbus
223 | 322 | A91_LOP_THRESHOLD_2ND_msk | Umbral Mínimo Temperatura Evaporación circuito 2 en driver | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -76 | 392 | °C/°F |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Threshold low evaporation temperature cicuit 2 in driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Umbral Mínimo Temperatura Evaporación circuito 2 en driver"}}} | [] | modbus
224 | 323 | A93_MOP_THRESHOLD_2ND_msk | Umbral Máximo Temperatura Evaporación - circuito 2 en driver | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 800 | °C/°F |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Threshold high evaporation temperature cicuit 2 in driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Umbral Máximo Temperatura Evaporación - circuito 2 en driver"}}} | [] | modbus
225 | 340 | A48_PID_Kp_msk | Parametros PID Banda Proporcional circuito 1 Driver | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 800 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"PID: proportional gain - circuit 1 in driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Parametros PID Banda Proporcional circuito 1 Driver"}}} | [] | modbus
226 | 341 | A49_PID_Td_msk | Tiempo derivativo del PID, circuito 1 en driver | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 800 | s |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"PID Derivative Time - circuit 1 in driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Tiempo derivativo del PID, circuito 1 en driver"}}} | [] | modbus
227 | 342 | A87_PID_Kp_2ND_msk | Parametros PID Banda Prop. Circuito 2 en driver | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 800 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"PID: proportional gain - cicuit 2 in driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Parametros PID Banda Prop. Circuito 2 en driver"}}} | [] | modbus
228 | 343 | A88_PID_Td_2ND_msk | Tiempo Derivativo Circuito 2 en driver | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 800 | s |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"PID: derivative time - cicuit 2 in driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Tiempo Derivativo Circuito 2 en driver"}}} | [] | modbus
229 | 344 | A55_LOW_SH_Ti_msk | Tiempo Integración del recalentamiento circuito 1 en driver | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 800 | s |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"LowSH: integral time - circuit 1 in driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Tiempo Integración del recalentamiento circuito 1 en driver"}}} | [] | modbus
230 | 345 | A51_LOP_Ti_msk | Tiempo de Integracion para baja Temperatura Evaporación cicu | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 800 | s |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"LOP: integral time low temperature of evaporation - circuit"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Tiempo de Integracion para baja Temperatura Evaporación cicu"}}} | [] | modbus
231 | 346 | A53_MOP_Ti_msk | Tiempo de Integración para Maxima temperatua de evaporacion | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 800 | s |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"MOP: integral time temperature of evaporation - circuit 1 in"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Tiempo de Integración para Maxima temperatua de evaporacion"}}} | [] | modbus
232 | 347 | A90_LOW_SH_Ti_2ND_msk | Tiempo Integración del recalentamiento circuito 2 en driver | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 800 | s |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"LowSH: integral time low superheat - cicuit 2 in driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Tiempo Integración del recalentamiento circuito 2 en driver"}}} | [] | modbus
233 | 348 | A92_LOP_Ti_2ND_msk | Tiempo de Integracion para baja Temperatura Evaporación cicu | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 800 | s |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"LOP: integral time low evaporation temperature - cicuit 2 in"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Tiempo de Integracion para baja Temperatura Evaporación cicu"}}} | [] | modbus
234 | 349 | A94_MOP_Ti_2ND_msk | Tiempo de Integración para Maxima temperatua de evaporacion | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 800 | s |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"MOP: integral time high evaporation temperature - cicuit 2 i"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Tiempo de Integración para Maxima temperatua de evaporacion"}}} | [] | modbus
235 | 350 | A58_HITCOND_THRESHOLD_msk | Umbral Alta temperatura Cond. del Circuito 1 en Driver | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -76 | 392 | °C/°F |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"High condensing temperature: thresold - circuit 1 in driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Umbral Alta temperatura Cond. del Circuito 1 en Driver"}}} | [] | modbus
236 | 351 | A57_HITCOND_Ti_msk | Tiempo Integración Alta temperatura Cond. del Circuito 1 en | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 800 | s |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"High condensing temperature: integral time - circuit 1 in dr"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Tiempo Integración Alta temperatura Cond. del Circuito 1 en"}}} | [] | modbus
237 | 368 | SH_Set_CH | Consigna Sobrecalentamiento Modo Frío, VEE en Driver | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 5 | 99.9 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"EEV SuperHeating setpoint on driver, Chiller mode"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna Sobrecalentamiento Modo Frío, VEE en Driver"}}} | [] | modbus
238 | 369 | Low_SH_Thrshd_CH | Umbral Baja Sobrecalentamiento Modo Frío, VEE en Driver | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 99.9 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"EEV Low SuperHeating threshold on driver, Chiller mode"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Umbral Baja Sobrecalentamiento Modo Frío, VEE en Driver"}}} | [] | modbus
239 | 370 | LOP_Thrshd_CH | Umbral Baja Temperatura Evaporación Modo Frío, VEE en Driver | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -60 | 99.9 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"EEV Low evaporating temp. threshold on driver, Chiller mode"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Umbral Baja Temperatura Evaporación Modo Frío, VEE en Driver"}}} | [] | modbus
240 | 371 | MOP_Thrshd_CH | Umbral Alta Temperatura Evaporación Modo Frío, VEE en Driver | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 999.9 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"EEV High evaporating temp. threshold on driver, Chiller mode"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Umbral Alta Temperatura Evaporación Modo Frío, VEE en Driver"}}} | [] | modbus
241 | 372 | SH_Set_HP | Consigna Sobrecalentamiento Modo Calor, VEE en Driver | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 5 | 99.9 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"EEV SuperHeating setpoint on driver, Heat mode"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna Sobrecalentamiento Modo Calor, VEE en Driver"}}} | [] | modbus
242 | 373 | Low_SH_Thrshd_HP | Umbral Baja Sobrecalentamiento Modo Frío, VEE en Driver | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 99.9 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"EEV Low SuperHeating threshold on driver, heat mode"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Umbral Baja Sobrecalentamiento Modo Frío, VEE en Driver"}}} | [] | modbus
243 | 374 | LOP_Thrshd_HP | Umbral Baja Temperatura Evaporación Modo Frío, VEE en driver | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -60 | 99.9 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"EEV Low evaporating temp. threshold on driver, Heat mode"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Umbral Baja Temperatura Evaporación Modo Frío, VEE en driver"}}} | [] | modbus
244 | 375 | MOP_Thrshd_HP | Umbral Alta Temperatura Evaporación Modo Frío, VEE en driver | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 999.9 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"EEV High evaporating temp. threshold on driver, Heat mode"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Umbral Alta Temperatura Evaporación Modo Frío, VEE en driver"}}} | [] | modbus
245 | 376 | SH_Set_DF | Consigna Sobrecalentamiento Desescarche, VEE en driver | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 5 | 99.9 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"EEV SuperHeating setpoint on driver, Defrost mode"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna Sobrecalentamiento Desescarche, VEE en driver"}}} | [] | modbus
246 | 377 | Low_SH_Thrshd_DF | Umbral Baja Sobrecalentamiento Desescarche, VEE en driver | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 99.9 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"EEV Low SuperHeating threshold on driver, Defrost mode"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Umbral Baja Sobrecalentamiento Desescarche, VEE en driver"}}} | [] | modbus
247 | 378 | LOP_Thrshd_DF | Umbral Baja Temperatura Evaporación Desescarche, VEE en driv | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -60 | 99.9 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"EEV Low evaporating temp. threshold on driver, Defrost mode"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Umbral Baja Temperatura Evaporación Desescarche, VEE en driv"}}} | [] | modbus
248 | 379 | MOP_Thrshd_DF | Umbral Alta Temperatura Evaporación Desescarche, VEE en driv | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 999.9 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"EEV High evaporating temp. threshold on driver, Defrost mode"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Umbral Alta Temperatura Evaporación Desescarche, VEE en driv"}}} | [] | modbus
249 | 391 | Serial_Temp_1 | Temperatura serial 1 | SERIAL PROBE |  | simple | 0 | 4 | 0 | -99.9 | 99.9 | °C |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Serial temp 1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura serial 1"}}} | [] | modbus
250 | 392 | Serial_Humid_1 | Humedad serial 1 | SERIAL PROBE |  | simple | 0 | 4 | 0 | 0 | 99.9 | %rH |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Serial humidity 1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Humedad serial 1"}}} | [] | modbus
251 | 394 | Serial_Temp_2 | Temperatura serial 2 | SERIAL PROBE |  | simple | 0 | 4 | 0 | -99.9 | 99.9 | °C |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Serial temp 2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura serial 2"}}} | [] | modbus
252 | 395 | Serial_Humid_2 | Humedad serial 2 | SERIAL PROBE |  | simple | 0 | 4 | 0 | 0 | 99.9 | %rH |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Serial humidity 2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Humedad serial 2"}}} | [] | modbus
253 | 397 | Serial_Temp_3 | Temperatura serial 3 | SERIAL PROBE |  | simple | 0 | 4 | 0 | -99.9 | 99.9 | °C |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Serial temp 3"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura serial 3"}}} | [] | modbus
254 | 398 | Serial_Humid_3 | Humedad serial 3 | SERIAL PROBE |  | simple | 0 | 4 | 0 | 0 | 99.9 | %rH |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Serial humidity 3"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Humedad serial 3"}}} | [] | modbus
255 | 400 | Serial_Temp_4 | Temperatura serial 4 | SERIAL PROBE |  | simple | 0 | 4 | 0 | -99.9 | 99.9 | °C |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Serial temp 4"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura serial 4"}}} | [] | modbus
256 | 401 | Serial_Humid_4 | Humedad serial 4 | SERIAL PROBE |  | simple | 0 | 4 | 0 | 0 | 99.9 | %rH |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Serial humidity 4"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Humedad serial 4"}}} | [] | modbus
257 | 403 | Serial_Temp_5 | Temperatura serial 5 | SERIAL PROBE |  | simple | 0 | 4 | 0 | -99.9 | 99.9 | °C |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Serial temp 5"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura serial 5"}}} | [] | modbus
258 | 404 | Serial_Humid_5 | Humedad serial 5 | SERIAL PROBE |  | simple | 0 | 4 | 0 | 0 | 99.9 | %rH |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Serial humidity 5"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Humedad serial 5"}}} | [] | modbus
259 | 406 | Serial_Temp_6 | Temperatura serial 6 | SERIAL PROBE |  | simple | 0 | 4 | 0 | -99.9 | 99.9 | °C |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Serial temp 6"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura serial 6"}}} | [] | modbus
260 | 407 | Serial_Humid_6 | Humedad serial 6 | SERIAL PROBE |  | simple | 0 | 4 | 0 | 0 | 99.9 | %rH |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Serial humidity 6"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Humedad serial 6"}}} | [] | modbus
261 | 409 | Req_Air_Quality | Demanda de calidad del aire | AIR QUALITY |  | simple | 0 | 4 | 0 | 0 | 999.9 | % |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Air quality demand"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Demanda de calidad del aire"}}} | [] | modbus
262 | 410 | Displayed_Temperature_msk | Temperatura mostrada en pantalla THTune | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -3276.8 | 3276.7 |  |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Temperature to show on the THTune display"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura mostrada en pantalla THTune"}}} | [] | modbus
263 | 411 | Displayed_Humidity_msk | Humedad mostradad en pantalla THTune | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 100 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Humidity to show on the THTune display"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Humedad mostradad en pantalla THTune"}}} | [] | modbus
264 | 412 | Temp_THTune_1 | Sonda Temperatura THTune 1 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 3276.7 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Temperature measured by the device probe"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Sonda Temperatura THTune 1"}}} | [] | modbus
265 | 415 | A105_DISCHARGE_TEMP_msk | Temperatura Descarga VEE en Driver | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -76 | 392 | °C/°F |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"EEV Temperature Discharge on Driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura Descarga VEE en Driver"}}} | [] | modbus
266 | 416 | A101_DISCHARGE_TEMP_SET_msk | Consigna Temperatura Descarga VEE en driver | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -76 | 392 | °C/°F |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"EEV Setpoint discharge temperature on drive"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna Temperatura Descarga VEE en driver"}}} | [] | modbus
267 | 421 | PwrOut_EBM_Imp | Potencia Ventilador Impulsión | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 3276.7 | W |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Current power in [W] for Ebmpapst supply fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Potencia Ventilador Impulsión"}}} | [] | modbus
268 | 422 | PwrOut_EBM_Ret | Potencia Ventilador Retorno | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 3276.7 | W |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Current power in [W] for Ebmpapst return fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Potencia Ventilador Retorno"}}} | [] | modbus
269 | 423 | ElectronicTemp_IR23 | Temperatura ambiente Electrónica Ventiladore Retorno o Impul | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -999.9 | 999.9 | °C |  | 0 | 0 | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Inside electronic ambient temperature"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura ambiente Electrónica Ventiladore Retorno o Impul"}}} | [] | modbus
270 | 429 | A12_HITCOND_COND_TEMP | Pantalla E/S Temperatura Condensación Regulacion Auxiliar Ha | PARAMETERS |  | simple | 0 | 3 | 6 | -76 | 392 | °C/°F |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Condensation Temperature I/O Display Auxiliary Regulation En"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Pantalla E/S Temperatura Condensación Regulacion Auxiliar Ha"}}} | [] | modbus
271 | 431 | Apparent_Power_H_SPV | Potencia Aparente | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 999.9 | kVA |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"es_ES":{"name":null,"_type":"languages","category":null,"description":"Potencia Aparente"}}} | [] | modbus
272 | 5002 | CAL_AIRE_CO2 | Calidad Aire Co2 | STATUS |  | basic | 60 | 4 | 0 | 0 | 9999 | ppm |  | 0 |  | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"CO2 level"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Calidad Aire Co2"}}} | [] | modbus
273 | 5003 | Work_comp | Nº Compresores Funcionando | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 10 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Number of working compressors"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Nº Compresores Funcionando"}}} | [] | modbus
274 | 5004 | HORAS_C11 | Horas Compresor 1 C1 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 |  |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Hours Compressor 1 C1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Horas Compresor 1 C1"}}} | [] | modbus
275 | 5005 | HORAS_C12 | Horas Compresor 1 C2 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 |  |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Hours Compressor 1 C2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Horas Compresor 1 C2"}}} | [] | modbus
276 | 5006 | HORAS_C13 | Horas Compresor 1 C3 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 |  |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Hours Compressor 1 C3"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Horas Compresor 1 C3"}}} | [] | modbus
277 | 5007 | HORAS_C21 | Horas Compresor 2 C1 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 |  |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Hours Compressor 2 C1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Horas Compresor 2 C1"}}} | [] | modbus
278 | 5008 | HORAS_C22 | Horas Compresor 2 C2 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 |  |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Hours Compressor 2 C2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Horas Compresor 2 C2"}}} | [] | modbus
279 | 5009 | HORAS_C23 | Horas Compresor 2 C3 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 |  |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Hours Compressor 2 C3"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Horas Compresor 2 C3"}}} | [] | modbus
280 | 5010 | HORAS_CR | Horas Compresor Circuito Recuperación | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 |  |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Hours Compressor recovery circuit"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Horas Compresor Circuito Recuperación"}}} | [] | modbus
281 | 5011 | ARRANQUES_C11 | Arranques Compresor 1 C1 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 |  |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Start Compressor 1 C1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Arranques Compresor 1 C1"}}} | [] | modbus
282 | 5012 | ARRANQUES_C12 | Arranques Compresor 1 C2 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 |  |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Start Compressor 1 C2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Arranques Compresor 1 C2"}}} | [] | modbus
283 | 5013 | ARRANQUES_C13 | Arranques Compresor 1 C3 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 |  |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Start Compressor 1 C3"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Arranques Compresor 1 C3"}}} | [] | modbus
284 | 5014 | ARRANQUES_C21 | Arranques Compresor 2 C1 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 |  |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Starts Compressor 2 C1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Arranques Compresor 2 C1"}}} | [] | modbus
285 | 5015 | ARRANQUES_C22 | Arranques Compresor 2 C2 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 |  |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Start Compressor 2 C2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Arranques Compresor 2 C2"}}} | [] | modbus
286 | 5016 | ARRANQUES_C23 | Arranques Compresor 2 C3 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 |  |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Start Compressor 2 C3"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Arranques Compresor 2 C3"}}} | [] | modbus
287 | 5017 | ARRANQUES_CR | Arranques Compresor Circuito Recuperación | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 |  |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Start Compressor recovery circuit"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Arranques Compresor Circuito Recuperación"}}} | [] | modbus
288 | 5019 | Caudal_Actual_Imp | Caudal Actual Ventilador Impulsión | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 32767 | m3/h |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Supply fan current flow"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Caudal Actual Ventilador Impulsión"}}} | [] | modbus
289 | 5020 | Caudal_Actual_Ret | Caudal Actual Ventilador Retorno | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 32767 | m3/h |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Return fan current flow"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Caudal Actual Ventilador Retorno"}}} | [] | modbus
290 | 5021 | Caudal_Actual_m3s | Caudal Actual Ventilador Impulsión | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 32767 | m3/h |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Supply fan current flow"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Caudal Actual Ventilador Impulsión"}}} | [] | modbus
291 | 5022 | Caudal_Actual_Imp_L | Caudal Actual Ventilador Impulsión | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 32767 | m3/h |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Supply fan current flow"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Caudal Actual Ventilador Impulsión"}}} | [] | modbus
292 | 5023 | Caudal_Actual_Imp_H | Caudal Actual Ventilador Impulsión | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 32767 | m3/h |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Supply fan current flow"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Caudal Actual Ventilador Impulsión"}}} | [] | modbus
293 | 5024 | Caudal_Actual_Ret_L | Caudal Actual Ventilador Impulsión | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 32767 | m3/h |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Supply fan current flow"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Caudal Actual Ventilador Impulsión"}}} | [] | modbus
294 | 5025 | Caudal_Actual_Ret_H | Caudal Actual Ventilador Impulsión | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 32767 | m3/h |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Supply fan current flow"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Caudal Actual Ventilador Impulsión"}}} | [] | modbus
295 | 5026 | CAUDAL_NOMINAL_H_cooling | Caudal Nominal H Ventilador Frio | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 32767 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Nominal Flow H cooling supply fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Caudal Nominal H Ventilador Frio"}}} | [] | modbus
296 | 5027 | CAUDAL_NOMINAL_H_heating | Caudal Nominal H Ventilador Calor | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 32767 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Nominal Flow H heating supply fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Caudal Nominal H Ventilador Calor"}}} | [] | modbus
297 | 5028 | CAUDAL_NOMINAL_L_cooling | Caudal Nominal L Ventilador Frio | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 32767 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Nominal flow L cooling supply fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Caudal Nominal L Ventilador Frio"}}} | [] | modbus
298 | 5029 | CAUDAL_NOMINAL_L_heating | Caudal Nominal L Ventilador Calor | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 32767 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Nominal flow L heating supply fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Caudal Nominal L Ventilador Calor"}}} | [] | modbus
299 | 5030 | CAUDAL_NOMINAL_H_cooling_2 | Caudal Nominal H Ventilador Frio Retorno | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 32767 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Nominal Flow H cooling return fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Caudal Nominal H Ventilador Frio Retorno"}}} | [] | modbus
300 | 5031 | CAUDAL_NOMINAL_H_heating_2 | Caudal Nominal H Ventlador Calor Retorno | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 32767 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Nominal Flow H heating return fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Caudal Nominal H Ventlador Calor Retorno"}}} | [] | modbus
301 | 5032 | CAUDAL_NOMINAL_L_cooling_2 | Caudal Nominal L Ventilador Frio Retorno | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 32767 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Nominal flow L cooling return fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Caudal Nominal L Ventilador Frio Retorno"}}} | [] | modbus
302 | 5033 | CAUDAL_NOMINAL_L_heating_2 | Caudal Nominal L Ventilador Calor Retorno | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 32767 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Nominal flow L heating return fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Caudal Nominal L Ventilador Calor Retorno"}}} | [] | modbus
303 | 5037 | I4_EEV_POSITION_STEPS_msk | Pasos de la VEE del circuito 1 en driver | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 9999 | steps |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Steps of the EEV of circuit 1 in driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Pasos de la VEE del circuito 1 en driver"}}} | [] | modbus
304 | 5038 | I8_REG_STATUS_msk | Estado en que se encuentra VEE en circuito 1 en driver | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 1 | 100 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Status of EEV of circuit 1 in driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Estado en que se encuentra VEE en circuito 1 en driver"}}} | [] | modbus
305 | 5039 | I49_EEV_POSITION_STEPS_2ND_msk | Pasos de la VEE en circuito 2 en driver | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 9999 | steps |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"EEV B steps of circuit 2 in driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Pasos de la VEE en circuito 2 en driver"}}} | [] | modbus
306 | 5040 | I51_REG_STATUS_2ND_msk | Estado Válvula de Expansión en circuito 2 en driver | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 1 | 100 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"EEV status of circuit 2 in driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Estado Válvula de Expansión en circuito 2 en driver"}}} | [] | modbus
307 | 5048 | RET_ARRANQUE_DESESCAR | Retardo Arranque Desescarche | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 999 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Start delay defrost"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Retardo Arranque Desescarche"}}} | [] | modbus
308 | 5049 | TIEMPO_MIN_DESESCAR | Tiempo Mínimo Desescarche | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 999 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Minimum time defrost"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Tiempo Mínimo Desescarche"}}} | [] | modbus
309 | 5050 | TIEMPO_MAX_DESESCAR | Tiempo Máximo Desescarche | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 999 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Maximum time defrost"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Tiempo Máximo Desescarche"}}} | [] | modbus
310 | 5051 | N_MAX_AL_DESESCARCHE | Nº Max De Alarmas | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 999 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Defrost Alarms N. max for alarm"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Nº Max De Alarmas"}}} | [] | modbus
311 | 5052 | TIEMPO_ENTRE_DESESCAR | Tiempo Entre Desescarches | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 999 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Defrost time Time between defrost"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Tiempo Entre Desescarches"}}} | [] | modbus
312 | 5053 | TIEMPO_INVER_VALV_CICLO | Tiempo Inversión Válvula Ciclo | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 999 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Reverse cycle time"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Tiempo Inversión Válvula Ciclo"}}} | [] | modbus
313 | 5054 | TIEMPO_DRIPING | Tiempo Driping | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 999 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Dripping time"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Tiempo Driping"}}} | [] | modbus
314 | 5055 | Force_Mode_Speed_Circ1 | Potencia Goteo en tiempos de desescarhces, Gec33 | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1000 |  |  | 0 | Gec33 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Driping power in defrost time"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Potencia Goteo en tiempos de desescarhces, Gec33"}}} | [] | modbus
315 | 5056 | DayWeek | Cálculo Día De La Semana Según Fecha Actual (1 Lunes, 2 Mart | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 7 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Day of week calculation based on current date (0: ---; 1: Mo"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Cálculo Día De La Semana Según Fecha Actual (1 Lunes, 2 Mart"}}} | [] | modbus
316 | 5057 | NEW_DAY | Dia Nuevo | CLOCK / TIMEDATE |  | simple | 0 | 3 | 6 | 1 | 31 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"New day"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Dia Nuevo"}}} | [] | modbus
317 | 5058 | NEW_MONTH | Mes Nuevo | CLOCK / TIMEDATE |  | simple | 0 | 3 | 6 | 1 | 12 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"New month"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Mes Nuevo"}}} | [] | modbus
318 | 5059 | NEW_YEAR | Año Nuevo | CLOCK / TIMEDATE |  | simple | 0 | 3 | 6 | 0 | 99 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"New year"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Año Nuevo"}}} | [] | modbus
319 | 5060 | NEW_HOUR | Hora Nueva | CLOCK / TIMEDATE |  | simple | 0 | 3 | 6 | 0 | 23 | h |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"New hour"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Hora Nueva"}}} | [] | modbus
320 | 5061 | NEW_MINUTE | Minuto Nuevo | CLOCK / TIMEDATE |  | simple | 0 | 3 | 6 | 0 | 59 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"New minute"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Minuto Nuevo"}}} | [] | modbus
321 | 5062 | F1_Start_Hour | Hora Arranque Fase 1 | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 24 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Start hour F1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Hora Arranque Fase 1"}}} | [] | modbus
322 | 5063 | F1_Start_Minute | Minuto Arranque Fase 1 | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 60 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Start minute F1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Minuto Arranque Fase 1"}}} | [] | modbus
323 | 5064 | F1_Set_Cool | Consigna Frio Fase 1 0=Off / 1= Consigna Confort / 2=Consign | ALARM |  | simple | 30 | 3 | 6 | 0 | 3 |  |  | 0 |  | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Cooling setpoint F1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna Frio Fase 1 0=Off / 1= Consigna Confort / 2=Consign"}}} | [] | modbus
324 | 5065 | F2_Start_Hour | Hora Arranque Fase 2 | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 24 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Start hour F2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Hora Arranque Fase 2"}}} | [] | modbus
325 | 5066 | F2_Start_Minute | Minuto Arranque Fase 2 | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 60 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Start minute F2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Minuto Arranque Fase 2"}}} | [] | modbus
326 | 5067 | F2_Set_Cool | Consigna Frio Fase 2 0=Off / 1= Consigna Confort / 2=Consign | ALARM |  | simple | 30 | 3 | 6 | 0 | 3 |  |  | 0 |  | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Cooling setpoint F2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna Frio Fase 2 0=Off / 1= Consigna Confort / 2=Consign"}}} | [] | modbus
327 | 5068 | F1_Set_Heat | Consigna Calor Fase 1 0=Off / 1= Consigna Confort / 2=Consig | ALARM |  | simple | 30 | 3 | 6 | 0 | 3 |  |  | 0 |  | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Heating setpoint F1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna Calor Fase 1 0=Off / 1= Consigna Confort / 2=Consig"}}} | [] | modbus
328 | 5069 | F2_Set_Heat | Consigna Calor Fase 2 0=Off / 1= Consigna Confort / 2=Consig | ALARM |  | simple | 30 | 3 | 6 | 0 | 3 |  |  | 0 |  | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Heating setpoint F2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna Calor Fase 2 0=Off / 1= Consigna Confort / 2=Consig"}}} | [] | modbus
329 | 5070 | Day_Scheduler_Setting | Dia A Configurar Del Horario 0=Lunes / 1=Martes / 2=Miercole | ALARM |  | simple | 30 | 3 | 6 | 0 | 7 |  |  | 0 |  | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Setting scheduler day"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Dia A Configurar Del Horario 0=Lunes / 1=Martes / 2=Miercole"}}} | [] | modbus
330 | 5071 | Day_Scheduler_Copy_Go | Copiar Horarios | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Copy scheduler"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Copiar Horarios"}}} | [] | modbus
331 | 5072 | Day_Scheduler_Copy | Copiar El Horario Al Día 0=Lunes / 1=Martes / 2=Miercoles / | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 7 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Copy scheduler day"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Copiar El Horario Al Día 0=Lunes / 1=Martes / 2=Miercoles /"}}} | [] | modbus
332 | 5073 | F3_Start_Hour | Hora Arranque Fase 3 | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 24 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Start hour F3"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Hora Arranque Fase 3"}}} | [] | modbus
333 | 5074 | F3_Start_Minute | Minuto Arranque Fase 3 | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 60 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Start minute F3"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Minuto Arranque Fase 3"}}} | [] | modbus
334 | 5075 | F4_Start_Minute | Minuto Arranque Fase 4 | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 60 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Start minute F4"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Minuto Arranque Fase 4"}}} | [] | modbus
335 | 5076 | F4_Start_Hour | Hora Arranque Fase 4 | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 24 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Start hour F4"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Hora Arranque Fase 4"}}} | [] | modbus
336 | 5077 | F3_Set_Cool | Consigna Frio Fase 3 0=Off / 1= Consigna Confort / 2=Consign | ALARM |  | simple | 30 | 3 | 6 | 0 | 3 |  |  | 0 |  | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Cooling setpoint F3"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna Frio Fase 3 0=Off / 1= Consigna Confort / 2=Consign"}}} | [] | modbus
337 | 5078 | F4_Set_Cool | Consigna Frio Fase 4 0=Off / 1= Consigna Confort / 2=Consign | ALARM |  | simple | 30 | 3 | 6 | 0 | 3 |  |  | 0 |  | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Cooling setpoint F4"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna Frio Fase 4 0=Off / 1= Consigna Confort / 2=Consign"}}} | [] | modbus
338 | 5079 | F3_Set_Heat | Consigna Calor Fase 3 0=Off / 1= Consigna Confort / 2=Consig | ALARM |  | simple | 30 | 3 | 6 | 0 | 3 |  |  | 0 |  | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Heating setpoint F3"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna Calor Fase 3 0=Off / 1= Consigna Confort / 2=Consig"}}} | [] | modbus
339 | 5080 | F4_Set_Heat | Consigna Calor Fase 4 0=Off / 1= Consigna Confort / 2=Consig | ALARM |  | simple | 30 | 3 | 6 | 0 | 3 |  |  | 0 |  | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Heating setpoint F4"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna Calor Fase 4 0=Off / 1= Consigna Confort / 2=Consig"}}} | [] | modbus
340 | 5081 | P3_Set_Cool | Consigna frío periodo 3 | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 3 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Period 3 cool set type"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna frío periodo 3"}}} | [] | modbus
341 | 5084 | Freecooling_heating_Mode | Modo Freecooling / Freeheating | DAMPERS |  | simple | 0 | 3 | 6 | 1 | 4 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Freecooling and freeheating mode"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Modo Freecooling / Freeheating"}}} | [] | modbus
342 | 5085 | HumSetP_THTune_1 | Define Valor Setpoint de Humedad | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 32767 | % |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Defines the humidity setpoint value"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Define Valor Setpoint de Humedad"}}} | [] | modbus
343 | 5086 | EDV_1.I4_EEV_POSITION_STEPS | Pasos VEE circuito 1 en driver | PARAMETERS |  | simple | 0 | 3 | 6 | 0 | 9999 | steps |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"steps of the EEV of circuit 1 in driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Pasos VEE circuito 1 en driver"}}} | [] | modbus
344 | 5087 | I8_REG_STATUS | Estado VEE circuito 1 en driver | PARAMETERS |  | simple | 0 | 3 | 6 | 0 | 20 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"EEV status of circuit 1 in driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Estado VEE circuito 1 en driver"}}} | [] | modbus
345 | 5088 | I49_EEV_POSITION_STEPS_2ND | Pasos VEE circuito 2 en driver | PARAMETERS |  | simple | 0 | 3 | 6 | 0 | 9999 | steps |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"steps of the EEV of circuit 2 in driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Pasos VEE circuito 2 en driver"}}} | [] | modbus
346 | 5089 | I51_REG_STATUS_2ND | Estado VEE circuito 2 en driver | PARAMETERS |  | simple | 0 | 3 | 6 | 0 | 20 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"EEV status of circuit 2 in driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Estado VEE circuito 2 en driver"}}} | [] | modbus
347 | 5092 | Fan1_Setpoint | Consigna ventilador 1 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 |  |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Setpoint fan 1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna ventilador 1"}}} | [] | modbus
348 | 5093 | Fan2_Setpoint | Consigna ventilador 2 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 |  |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Setpoint fan 2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna ventilador 2"}}} | [] | modbus
349 | 5094 | Fan3_Setpoint | Consigna ventilador 3 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 |  |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Setpoint fan 3"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna ventilador 3"}}} | [] | modbus
350 | 5110 | Circuit_Num | Número De Circuitos En La Unidad | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 1 | 3 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Number of circuit in the unit"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Número De Circuitos En La Unidad"}}} | [] | modbus
351 | 5113 | Estados_1 | Estados 1 , array (+) | STATUS |  | basic | 60 | 4 | 0 | 0 | 9999 |  |  | 0 |  | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Status 1, array"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Estados 1 , array (+)"}}} | [] | modbus
352 | 5114 | Estados_2 | Estados 2, array | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 9999 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Status 2 array"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Estados 2, array"}}} | [] | modbus
353 | 5115 | SpeedReq_EBM_1 | Requisitos Velocidad [Rpm/%/V] Para Ventilador Ebmpapst 1 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 |  |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Speed input in [rpm/%/V] according to the control mode for E"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Requisitos Velocidad [Rpm/%/V] Para Ventilador Ebmpapst 1"}}} | [] | modbus
354 | 5116 | SpeedReq_EBM_2 | Requisitos Velocidad [Rpm/%/V] Para Ventilador Ebmpapst 2 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 |  |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Speed input in [rpm/%/V] according to the control mode for E"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Requisitos Velocidad [Rpm/%/V] Para Ventilador Ebmpapst 2"}}} | [] | modbus
355 | 5117 | SpeedReq_EBM_3 | Requisitos Velocidad [Rpm/%/V] Para Ventilador Ebmpapst 3 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 |  |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Speed input in [rpm/%/V] according to the control mode for E"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Requisitos Velocidad [Rpm/%/V] Para Ventilador Ebmpapst 3"}}} | [] | modbus
356 | 5118 | Potencia_Frig_E | Potencia Frigorifica Parte Entera, si esta habilitado el med | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 32767 | KW |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Refrigeration capacity integer, if energy metering or Therma"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Potencia Frigorifica Parte Entera, si esta habilitado el med"}}} | [] | modbus
357 | 5119 | Potencia_Frig_D | Potencia Frigorifica Parte Decimal, , si esta habilitado el | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 32767 | KW |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Refrigeration capacity decimal , if energy metering or Therm"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Potencia Frigorifica Parte Decimal, , si esta habilitado el"}}} | [] | modbus
358 | 5120 | Potencia_Frig_Sensible_E | Potencia Frigorifica Sensible Parte Entera, si esta habilita | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 32767 | KW |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Sensible refrigeration capacity integer, if energy metering "},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Potencia Frigorifica Sensible Parte Entera, si esta habilita"}}} | [] | modbus
359 | 5121 | Potencia_Frig_Sensible_D | Potencia Frigorifica Sensible Parte Decimal, si esta habilit | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 32767 | KW |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Sensible refrigeration capacity decimal, if energy metering "},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Potencia Frigorifica Sensible Parte Decimal, si esta habilit"}}} | [] | modbus
360 | 5122 | Potencia_Frig_Latente_E | Potencia Frigorifica Latente Parte Entera, si esta habilitad | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 32767 | KW |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Latent refrigeration capacity integer, if energy metering or"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Potencia Frigorifica Latente Parte Entera, si esta habilitad"}}} | [] | modbus
361 | 5123 | Potencia_Frig_Latente_D | Potencia Frigorifica Latente Parte Decimal , si esta habilit | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 32767 | KW |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Latent refrigeration capacity decimal, if energy metering or"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Potencia Frigorifica Latente Parte Decimal , si esta habilit"}}} | [] | modbus
362 | 5124 | COP | Coeficiente De Eficiencia De Calor, si esta habilitado el me | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 32767 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Coefficient of performance, if energy metering or Thermal is"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Coeficiente De Eficiencia De Calor, si esta habilitado el me"}}} | [] | modbus
363 | 5125 | EER | Coeficiente De Eficiencia De Frío, si esta habilitado el med | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 32767 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Energy efficiency ratio, if energy metering or Thermal is en"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Coeficiente De Eficiencia De Frío, si esta habilitado el med"}}} | [] | modbus
364 | 5134 | Apparent_Energy_L_MSK | Energía Aparente L (Valor Usado En Máscara), , si esta habil | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 999 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Apparent Energy L, if energy metering is enabled"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Energía Aparente L (Valor Usado En Máscara), , si esta habil"}}} | [] | modbus
365 | 5135 | Apparent_Energy_M_MSK | Energía Aparente M (Valor Usado En Máscara), si esta habilit | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 9999 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Apparent Energy M, if energy metering is enabled"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Energía Aparente M (Valor Usado En Máscara), si esta habilit"}}} | [] | modbus
366 | 5136 | Apparent_Energy_H_MSK | Energía Aparente H (Valor Usado En Máscara), si esta habilit | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 9999 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Apparent Energy H, if energy metering is enabled"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Energía Aparente H (Valor Usado En Máscara), si esta habilit"}}} | [] | modbus
367 | 5137 | Energy_L_MSK | Energía L (Valor Máscara), si esta habilitado el medido de e | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 999 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Energy L, if energy metering is enabled"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Energía L (Valor Máscara), si esta habilitado el medido de e"}}} | [] | modbus
368 | 5138 | Energy_M_MSK | Energía M (Valor Máscara), si esta habilitado el medido de e | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 9999 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Energy M, if energy metering is enabled"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Energía M (Valor Máscara), si esta habilitado el medido de e"}}} | [] | modbus
369 | 5139 | Energy_H_MSK | Energía H (Valor Máscara), si esta habilitado el medido de e | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 9999 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Energy H, if energy metering is enabled"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Energía H (Valor Máscara), si esta habilitado el medido de e"}}} | [] | modbus
370 | 5140 | F_MIN | Factor Mínimo Flujo Ventilador, si esta habilitado el medido | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 100 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Minimum fan flow factor, if energy metering is enabled"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Factor Mínimo Flujo Ventilador, si esta habilitado el medido"}}} | [] | modbus
371 | 5141 | RET_PRIMER_DESESCAR | Retorno Primer Desescarche | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 999 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"First defrost return"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Retorno Primer Desescarche"}}} | [] | modbus
372 | 5142 | CURRENT_HOUR | Hora Actual | CLOCK / TIMEDATE |  | simple | 0 | 4 | 0 | 0 | 23 | h |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Current hour"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Hora Actual"}}} | [] | modbus
373 | 5143 | CURRENT_MINUTE | Minuto Actual | CLOCK / TIMEDATE |  | simple | 0 | 4 | 0 | 0 | 59 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Current minute"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Minuto Actual"}}} | [] | modbus
374 | 5144 | HORAS_UNIDAD | Horas De Funcionamiento | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 |  |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Working hours"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Horas De Funcionamiento"}}} | [] | modbus
375 | 5145 | ARRANQUES_UNIDAD | Arranques De La Máquina | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 |  |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Start-ups number"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Arranques De La Máquina"}}} | [] | modbus
376 | 5149 | DST_Minute | * 0001, Tiempo transcisión | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 32767 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"* 0001, Transition time"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"* 0001, Tiempo transcisión"}}} | [] | modbus
377 | 5150 | Srt_DST_MonthW | * 0002, Comienzo semanal durante mes | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 32767 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"* 0002, Start weekly in one month"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"* 0002, Comienzo semanal durante mes"}}} | [] | modbus
378 | 5151 | Srt_DST_Week | * 0003, Dia comienzo durante semana | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 32767 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"* 0003, Start day in one week"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"* 0003, Dia comienzo durante semana"}}} | [] | modbus
379 | 5152 | Srt_DST_Month | * 0004, Mes comienzo | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 32767 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"* 0004, Start month"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"* 0004, Mes comienzo"}}} | [] | modbus
380 | 5153 | Srt_DST_Hour | * 0005, Hora comienzo | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 32767 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"* 0005, Start hour"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"* 0005, Hora comienzo"}}} | [] | modbus
381 | 5155 | PresionImpulsion | Diferencial de la presión del Ventilador Impulsión | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 32767 | Pa |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Supply Fan Pressure diff."},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Diferencial de la presión del Ventilador Impulsión"}}} | [] | modbus
382 | 5160 | End_DST_MonthW | * 0006, Finalización semanal durante mes | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 32767 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"* 0006, End weekly in one month"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"* 0006, Finalización semanal durante mes"}}} | [] | modbus
383 | 5161 | End_DST_Week | * 0007, Día finalización durante semana | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 32767 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"* 0007, End day in one week"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"* 0007, Día finalización durante semana"}}} | [] | modbus
384 | 5162 | HORAS_C31 | Horas Compresor 3 C1 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 |  |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Hours compressor 3 circuit 1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Horas Compresor 3 C1"}}} | [] | modbus
385 | 5163 | HORAS_C32 | Horas Compresor 3 C2 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 |  |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Hours compressor 3 circuit 2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Horas Compresor 3 C2"}}} | [] | modbus
386 | 5164 | End_DST_Month | * 0008, Mes finalización | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 32767 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"* 0008, End month"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"* 0008, Mes finalización"}}} | [] | modbus
387 | 5165 | ARRANQUES_C31 | Arranques Compresor 3 C1 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 |  |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Start-ups compressor 3 circuit 1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Arranques Compresor 3 C1"}}} | [] | modbus
388 | 5166 | ARRANQUES_C32 | Arranques Compresor 3 C2 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 |  |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Start-ups compressor 3 circuit 2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Arranques Compresor 3 C2"}}} | [] | modbus
389 | 5167 | End_DST_Hour | * 0009, Hora finalización | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 32767 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"* 0009, End hour"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"* 0009, Hora finalización"}}} | [] | modbus
390 | 5168 | Setp_Reg_CO2 | Consigna regulación CO2 | AIR QUALITY |  | simple | 0 | 3 | 6 | 0 | 5000 | ppm |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"CO2 regulation setpoint"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna regulación CO2"}}} | [] | modbus
391 | 5169 | Diff_Reg_CO2 | Diferencial regulación CO2 | AIR QUALITY |  | simple | 0 | 3 | 6 | 0 | 2000 | ppm |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"CO2 regulation differential"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Diferencial regulación CO2"}}} | [] | modbus
392 | 5170 | Setp_Reg_VOC | Consigna regulación VOC | AIR QUALITY |  | simple | 0 | 3 | 6 | 0 | 100 | % |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"VOC regulation setpoint"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna regulación VOC"}}} | [] | modbus
393 | 5171 | Diff_Reg_VOC | Diferencial regulación VOC | AIR QUALITY |  | simple | 0 | 3 | 6 | 0 | 100 | % |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"VOC regulation differential"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Diferencial regulación VOC"}}} | [] | modbus
394 | 5172 | P_DIF_IMP_RET | Diferencia Presion Impulsión-Retorno | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 | Pa |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Supply / Return pressure differential"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Diferencia Presion Impulsión-Retorno"}}} | [] | modbus
395 | 5173 | MAX_P_DIF_IMP_RET | Límite Máximo Diferencial Presión Impulsión-Retorno | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 32767 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Supply / Return pressure differential maximum"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Límite Máximo Diferencial Presión Impulsión-Retorno"}}} | [] | modbus
396 | 5174 | PotenciaVImpulsion | Potencia del Ventilador de Impulsion | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 32767 | W |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Supply Fan Power"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Potencia del Ventilador de Impulsion"}}} | [] | modbus
397 | 5175 | DC_VImpulsion | Corriente Continua Ventilador Impulsion | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 32767 | V |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Direct Current (DC) supply Fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Corriente Continua Ventilador Impulsion"}}} | [] | modbus
398 | 5176 | P1_Start_Day | Día comienzo periodo 1 | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 31 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Period 1 start day"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Día comienzo periodo 1"}}} | [] | modbus
399 | 5177 | VelocidadVImpulsion | Velocidad Ventilador de Impulsion | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 32767 | rpm |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Direct Current (DC) for Impulse Fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Velocidad Ventilador de Impulsion"}}} | [] | modbus
400 | 5178 | PotenciaVRetorno | Potencia ventilador Retorno | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 32767 | W |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Return Fan Power"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Potencia ventilador Retorno"}}} | [] | modbus
401 | 5179 | DC_VRetorno | Corriente Continua Ventilador Retorno | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 32767 | V |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Direct Current (DC) Return Fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Corriente Continua Ventilador Retorno"}}} | [] | modbus
402 | 5180 | ElectrTemp_EBM_Ret | Temperatura ventilador interior EBM | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 999 | °C |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"temperature for Internal Ebmpapst fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura ventilador interior EBM"}}} | [] | modbus
403 | 5181 | VelocidadVRetorno | Velocidad del Ventilador de Retorno | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 32767 | rpm |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Return Fan Speed"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Velocidad del Ventilador de Retorno"}}} | [] | modbus
404 | 5182 | HORAS_ET1 | Horas Etapa Resistencias 1 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 |  |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Resistances hours stage 1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Horas Etapa Resistencias 1"}}} | [] | modbus
405 | 5183 | HORAS_ET2 | Horas Etapa Resistencias 2 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 |  |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Resistances hours stage 2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Horas Etapa Resistencias 2"}}} | [] | modbus
406 | 5184 | HORAS_V_IMP | Horas Funcionamiento ventilador Impulsión | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 |  |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Supply fan working hours"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Horas Funcionamiento ventilador Impulsión"}}} | [] | modbus
407 | 5185 | HORAS_V_RET | Horas Funcionamiento ventilador Retorno | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 |  |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Return fan working hours"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Horas Funcionamiento ventilador Retorno"}}} | [] | modbus
408 | 5186 | HORAS_V_EXT_1 | Horas Funcionamiento Ventilador Exterior 1 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 |  |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"External fan 1 working hours"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Horas Funcionamiento Ventilador Exterior 1"}}} | [] | modbus
409 | 5187 | HORAS_V_EXT_2 | Horas Funcionamiento Ventilador Exterior 2 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 |  |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"External fan 2 working hours"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Horas Funcionamiento Ventilador Exterior 2"}}} | [] | modbus
410 | 5188 | HORAS_V_EXT_3 | Horas Funcionamiento Ventilador Exterior 3 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 |  |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"External fan 3 working hours"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Horas Funcionamiento Ventilador Exterior 3"}}} | [] | modbus
411 | 5198 | UnitStatus | Estado Unidad (0: -; 1: -; 2: OffByALR; 3: OffByNETWORK; 4: | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 99 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Unit Status (0: - Waiting ; 1: Unit On-; 2: OffByAlarm; 3: O"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Estado Unidad (0: -; 1: -; 2: OffByALR; 3: OffByNETWORK; 4:"}}} | [] | modbus
412 | 5199 | P1_Start_Month | Comienzo mes periodo 1 | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 12 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Period 1 start month"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Comienzo mes periodo 1"}}} | [] | modbus
413 | 5200 | P1_Stop_Day | Día parada periodo 1 | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 31 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Period 1 stop day"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Día parada periodo 1"}}} | [] | modbus
414 | 5201 | P1_Stop_Month | Mes parada periodo 1 | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 12 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Period 1 stop month"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Mes parada periodo 1"}}} | [] | modbus
415 | 5202 | P1_Set_Cool | Consigna frío periodo 1 | ALARM |  | simple | 30 | 3 | 6 | 0 | 3 |  |  | 0 |  | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Period 1 cool set type"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna frío periodo 1"}}} | [] | modbus
416 | 5204 | P1_Set_Heat | Consigna calor periodo 1 | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 3 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Period 1 heating setting"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna calor periodo 1"}}} | [] | modbus
417 | 5205 | P1_Start_Days_Num | Número máximo de días P1_Start_Month | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 1 | 31 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Max number of days for P1_Start_Month"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Número máximo de días P1_Start_Month"}}} | [] | modbus
418 | 5206 | P1_Stop_Days_Num | Número máximo de días P1_Stop_Month | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 1 | 31 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Max number of days for P1_Stop_Month"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Número máximo de días P1_Stop_Month"}}} | [] | modbus
419 | 5207 | P2_Start_Day | Día comienzo periodo 2 | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 31 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Period 2 start day"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Día comienzo periodo 2"}}} | [] | modbus
420 | 5208 | P2_Start_Month | Mes comienzo periodo 2 | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 12 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Period 2 start month"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Mes comienzo periodo 2"}}} | [] | modbus
421 | 5209 | P2_Stop_Day | Día parada periodo 2 | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 31 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Period 2 stop day"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Día parada periodo 2"}}} | [] | modbus
422 | 5210 | P2_Stop_Month | Mes parada periodo 2 | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 12 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Period 2 start month"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Mes parada periodo 2"}}} | [] | modbus
423 | 5211 | P2_Set_Cool | Consigna frío periodo 2 | ALARM |  | simple | 30 | 3 | 6 | 0 | 3 |  |  | 0 |  | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Period 2 cool set type"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna frío periodo 2"}}} | [] | modbus
424 | 5212 | P2_Set_Heat | Consigna calor periodo 2 | ALARM |  | simple | 30 | 3 | 6 | 0 | 3 |  |  | 0 |  | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Period 2 heating setting"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna calor periodo 2"}}} | [] | modbus
425 | 5213 | P2_Stop_Days_Num | Número máximo de días P2_Stop_Month | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 1 | 31 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Max number of days for P2_Stop_Month"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Número máximo de días P2_Stop_Month"}}} | [] | modbus
426 | 5214 | P2_Start_Days_Num | Número máximo de días P2_Start_Month | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 1 | 31 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Max number of days for P2_Start_Month"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Número máximo de días P2_Start_Month"}}} | [] | modbus
427 | 5215 | P3_Start_Day | Día comienzo periodo 3 | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 31 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Period 3 start day"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Día comienzo periodo 3"}}} | [] | modbus
428 | 5216 | P3_Start_Month | Mes comienzo periodo 3 | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 12 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Period 3 start month"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Mes comienzo periodo 3"}}} | [] | modbus
429 | 5217 | P3_Stop_Day | Día parada periodo 3 | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 31 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Period 3 stop day"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Día parada periodo 3"}}} | [] | modbus
430 | 5218 | P3_Stop_Month | Mes parada periodo 3 | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 12 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Period 3 stop month"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Mes parada periodo 3"}}} | [] | modbus
431 | 5219 | P3_Set_Heat | Consigna calor periodo 3 | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 3 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Period 3 heating setting"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna calor periodo 3"}}} | [] | modbus
432 | 5220 | P3_Start_Days_Num | Número máximo de días P3_Start_Month | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 1 | 31 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Max number of days for P3_Start_Month"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Número máximo de días P3_Start_Month"}}} | [] | modbus
433 | 5221 | P3_Stop_Days_Num | Número máximo de días P3_Stop_Month | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 1 | 31 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Max number of days for P3_Stop_Month"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Número máximo de días P3_Stop_Month"}}} | [] | modbus
434 | 5222 | SD1_Day | Special day 1 día | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 31 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Special day 1 day"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Special day 1 día"}}} | [] | modbus
435 | 5223 | SD1_Month | Special day 1 mes | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 12 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Special day 1 month"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Special day 1 mes"}}} | [] | modbus
436 | 5224 | SD1_Set_Cool | Special day 1 consigna frío | ALARM |  | simple | 30 | 3 | 6 | 0 | 3 |  |  | 0 |  | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Special day 1 cool type"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Special day 1 consigna frío"}}} | [] | modbus
437 | 5225 | SD1_Set_Heat | Special day 1 consigna calor | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 3 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Special day 1 heating setting"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Special day 1 consigna calor"}}} | [] | modbus
438 | 5226 | SD1_Num | Número máximo de días SD1_Month | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 1 | 31 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Max number of days for SD1_Month"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Número máximo de días SD1_Month"}}} | [] | modbus
439 | 5227 | SD2_Day | Special day 2 día | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 31 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Special day 2 day"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Special day 2 día"}}} | [] | modbus
440 | 5228 | SD2_Month | Special day 2 mes | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 12 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Special day 2 month"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Special day 2 mes"}}} | [] | modbus
441 | 5229 | SD2_Set_Cool | Special day 2 consigna frío | ALARM |  | simple | 30 | 3 | 6 | 0 | 3 |  |  | 0 |  | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Special day 2 cool set type"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Special day 2 consigna frío"}}} | [] | modbus
442 | 5230 | SD2_Set_Heat | Special day 2 consigna calor | ALARM |  | simple | 30 | 3 | 6 | 0 | 3 |  |  | 0 |  | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Special day 2 heating setting"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Special day 2 consigna calor"}}} | [] | modbus
443 | 5231 | SD2_Num | Número máximo de días SD2_Month | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 1 | 31 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Max number of days for SD2_Month"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Número máximo de días SD2_Month"}}} | [] | modbus
444 | 5232 | SD3_Day | Special day 3 día | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 31 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Special day 3 day"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Special day 3 día"}}} | [] | modbus
445 | 5233 | SD3_Month | Special day 3 mes | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 12 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Special day 3 month"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Special day 3 mes"}}} | [] | modbus
446 | 5234 | SD3_Set_Cool | Special day 3 consigna frío | ALARM |  | simple | 30 | 3 | 6 | 0 | 3 |  |  | 0 |  | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Special day 3 cool set type"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Special day 3 consigna frío"}}} | [] | modbus
447 | 5235 | SD3_Set_Heat | Special day 3 consigna calor | ALARM |  | simple | 30 | 3 | 6 | 0 | 3 |  |  | 0 |  | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Special day 3 heating setting"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Special day 3 consigna calor"}}} | [] | modbus
448 | 5236 | SD3_Num | Número máximo de días SD3_Month | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 1 | 31 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Max number of days for SD3_Month"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Número máximo de días SD3_Month"}}} | [] | modbus
449 | 5237 | SD4_Day | Special day 4 día | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 31 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Special day 4 day"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Special day 4 día"}}} | [] | modbus
450 | 5238 | SD4_Month | Special day 4 mes | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 12 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Special day 4 month"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Special day 4 mes"}}} | [] | modbus
451 | 5239 | SD4_Num | Número máximo de días SD4_Month | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 1 | 31 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Max number of days for SD4_Month"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Número máximo de días SD4_Month"}}} | [] | modbus
452 | 5240 | SD4_Set_Cool | Special day 4 consigna frío | ALARM |  | simple | 30 | 3 | 6 | 0 | 3 |  |  | 0 |  | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Special day 4 cool set type"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Special day 4 consigna frío"}}} | [] | modbus
453 | 5241 | SD4_Set_Heat | Special day 4 consigna calor | ALARM |  | simple | 30 | 3 | 6 | 0 | 3 |  |  | 0 |  | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Special day 4 heating setting"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Special day 4 consigna calor"}}} | [] | modbus
454 | 5242 | SD5_Day | Special day 5 día | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 31 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Special day 5 day"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Special day 5 día"}}} | [] | modbus
455 | 5243 | SD5_Month | Special day 5 mes | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 12 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Special day 5 month"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Special day 5 mes"}}} | [] | modbus
456 | 5244 | SD5_Num | Número máximo de días SD5_Month | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 1 | 31 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Max number of days for SD5_Month"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Número máximo de días SD5_Month"}}} | [] | modbus
457 | 5245 | SD5_Set_Cool | Special day 5 consigna frío | ALARM |  | simple | 30 | 3 | 6 | 0 | 3 |  |  | 0 |  | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Special day 5 cool set type"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Special day 5 consigna frío"}}} | [] | modbus
458 | 5246 | SD5_Set_Heat | Special day 5 consigna calor | ALARM |  | simple | 30 | 3 | 6 | 0 | 3 |  |  | 0 |  | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Special day 5 heating setting"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Special day 5 consigna calor"}}} | [] | modbus
459 | 5247 | SD6_Day | Special day 6 día | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 31 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Special day 6 day"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Special day 6 día"}}} | [] | modbus
460 | 5248 | SD6_Month | Special day 6 mes | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 12 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Special day 6 month"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Special day 6 mes"}}} | [] | modbus
461 | 5249 | SD6_Num | Número máximo de días SD6_Month | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 1 | 31 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Max number of days for SD6_Month"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Número máximo de días SD6_Month"}}} | [] | modbus
462 | 5250 | SD6_Set_Cool | Special day 6 consigna frío | ALARM |  | simple | 30 | 3 | 6 | 0 | 3 |  |  | 0 |  | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Special day 6 cool set type"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Special day 6 consigna frío"}}} | [] | modbus
463 | 5251 | SD6_Set_Heat | Special day 6 consigna calor | ALARM |  | simple | 30 | 3 | 6 | 0 | 3 |  |  | 0 |  | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Special day 6 heating setting"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Special day 6 consigna calor"}}} | [] | modbus
464 | 5254 | EDV_2.I49_EEV_POSITION_STEPS_2ND_msk | Posición VEE - Circuito 3 en driver | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 9999 | steps |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"EEV position - Circuit 3 from driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Posición VEE - Circuito 3 en driver"}}} | [] | modbus
465 | 5255 | EDV_2.I51_REG_STATUS_2ND_msk | Posición VEE - Circuito 4 en driver | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 1 | 100 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"EEV status - Circuito 4 from driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Posición VEE - Circuito 4 en driver"}}} | [] | modbus
466 | 5257 | Sensor_NIC_Imp | Sensor captador de presión de Ventilador de Impusión Nicotra | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 9999 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Pressure Sensor for Nicotra supply Fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Sensor captador de presión de Ventilador de Impusión Nicotra"}}} | [] | modbus
467 | 5260 | Sensor_NIC_Ret | Sensor captador de presión Ventilador Retorno de Nicotra | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 9999 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Pressure Sensor for Nicotra Return Fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Sensor captador de presión Ventilador Retorno de Nicotra"}}} | [] | modbus
468 | 5262 | Set_Airflow_Screen | Valor del Caudal de aire de los ventiladores Nicotra de impu | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 5000 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Air Flow Value for Nicotra Impulse Fans, Constant Flow Displ"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Valor del Caudal de aire de los ventiladores Nicotra de impu"}}} | [] | modbus
469 | 5263 | CurrSpeed_rpm | Velocidad actual ventilador [rpm] | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 32767 | rpm |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Actual speed [rpm] of the fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Velocidad actual ventilador [rpm]"}}} | [] | modbus
470 | 5264 | Voltage_L1_L2_L_SPV | Voltaje L1-L2 con medidor de energía | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 9999 | V |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Voltaje L1-L2 with energy meter"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Voltaje L1-L2 con medidor de energía"}}} | [] | modbus
471 | 5265 | Voltage_L2_L3_L_SPV | Voltaje L2-L3 con medidor de energía | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 9999 | V |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Voltaje L2-L3 with energy meter"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Voltaje L2-L3 con medidor de energía"}}} | [] | modbus
472 | 5266 | Voltage_L3_L1_L_SPV | Voltaje L3-L1con medidor de energía | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 9999 | V |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Voltaje L3-L1 with energy meter"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Voltaje L3-L1con medidor de energía"}}} | [] | modbus
473 | 5267 | Voltage_Average | Voltaje medio with energy meter | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 9999 | V |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Voltaje medio with energy meter"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Voltaje medio with energy meter"}}} | [] | modbus
474 | 5268 | Voltage_L_L_SPV | Voltaje V-L con medidor de energía | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 9999 | V |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Voltaje V-L with energy meter"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Voltaje V-L con medidor de energía"}}} | [] | modbus
475 | 5269 | Voltage_1_L_SPV | Voltaje 1 con medidor de energía | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 9999 | V |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Voltaje 1 with energy meter"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Voltaje 1 con medidor de energía"}}} | [] | modbus
476 | 5270 | Voltage_2_L_SPV | Voltaje 2 con medidor de energía | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 9999 | V |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Voltaje 2 with energy meter"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Voltaje 2 con medidor de energía"}}} | [] | modbus
477 | 5271 | Voltage_3_L_SPV | Voltaje 3 con medidor de energía | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 9999 | V |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Voltaje 3 with energy meter"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Voltaje 3 con medidor de energía"}}} | [] | modbus
478 | 5272 | Voltage_L_N_SPV | Voltaje V-N con medidor de energía | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 9999 | V |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Voltaje V-N with energy meter"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Voltaje V-N con medidor de energía"}}} | [] | modbus
479 | 5281 | IniReqChange | Demanda inicial 2 de compresores Fullinverter | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | -32768 | 32767 |  |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Initial Demand 2 for Full Inverter Compressors"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Demanda inicial 2 de compresores Fullinverter"}}} | [] | modbus
480 | 5282 | F_MIN_PGD | Caudal Mínimo ventilador impulsion EBM PGD | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 100 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Minimum Flow Rate of EBM PGD Impulse Fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Caudal Mínimo ventilador impulsion EBM PGD"}}} | [] | modbus
481 | 5284 | Diff_Reg_NZ | Zona neutra regulacion ventilador Impulsion EBM | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 1 | 9999 | °C |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Neutral Zone Regulation of EBM Impulse Fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Zona neutra regulacion ventilador Impulsion EBM"}}} | [] | modbus
482 | 5285 | Diff_Reg_Incr | Incremento Diferencial Zona Muerta regulación para activació | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 1 | 9999 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Increment Dead Zone Differential for Activation of EBM Impul"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Incremento Diferencial Zona Muerta regulación para activació"}}} | [] | modbus
483 | 5286 | Diff_Reg_Decr | Decremento Diferencial Zona Muerta regulación para activació | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 1 | 9999 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Dead Zone Differential Decrement for Activation of Regulatio"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Decremento Diferencial Zona Muerta regulación para activació"}}} | [] | modbus
484 | 5293 | Min_RPM | minima velocidad en rpm control Ventiladores Nicrota | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 9999 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Minimum Speed in RPM - Nicotra Fan Control"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"minima velocidad en rpm control Ventiladores Nicrota"}}} | [] | modbus
485 | 5294 | Max_RPM | maxima velocidad en rpm ventiladores Nicotra | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 9999 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Maximum Speed in RPM - Nicotra Fans"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"maxima velocidad en rpm ventiladores Nicotra"}}} | [] | modbus
486 | 5301 | HORAS_C33 | Horas compresor 3 C3 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 |  |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Hours compressor 3 circuit 3"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Horas compresor 3 C3"}}} | [] | modbus
487 | 5302 | ARRANQUES_C33 | Arranques compresor 3 C3 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 |  |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Start-ups compressor 3 circuit 3"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Arranques compresor 3 C3"}}} | [] | modbus
488 | 5303 | Int_Time_Temp | Tiempo Integración - Regulación Temperatura | SERVICES |  | simple | 0 | 3 | 6 | 0 | 999 | s |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Integration Time - Temperature Regulation"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Tiempo Integración - Regulación Temperatura"}}} | [] | modbus
489 | 5304 | Der_Time_Temp | Tiempo Derivación Regulación Temperatura | SERVICES |  | simple | 0 | 3 | 6 | 0 | 999 | s |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Derivative Time - Temperature Regulation"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Tiempo Derivación Regulación Temperatura"}}} | [] | modbus
490 | 5305 | Int_Time_Hum | Tiempo Integración - Regulación Humedad | SERVICES |  | simple | 0 | 3 | 6 | 0 | 999 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Humidity regulation integral time"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Tiempo Integración - Regulación Humedad"}}} | [] | modbus
491 | 5306 | Der_Time_Hum | Tiempo Derivativo - Regulación Humedad | SERVICES |  | simple | 0 | 3 | 6 | 0 | 999 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Humidity regulation derivative time"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Tiempo Derivativo - Regulación Humedad"}}} | [] | modbus
492 | 5307 | T_MAX_VEL_COND_CIRC1 | Tiempo a maxima velocidad control presión Ventilador Exteri | SERVICES |  | simple | 0 | 3 | 6 | 0 | 32000 | s |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Time to Maximum Speed Pressure Control External Fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Tiempo a maxima velocidad control presión Ventilador Exteri"}}} | [] | modbus
493 | 5308 | HumSetP_Min_THTune_1 | Consigna humedad mínima | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1000 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Lower limit of the humidity setpoint value"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna humedad mínima"}}} | [] | modbus
494 | 5309 | HumSetP_Max_THTune_1 | Consigna humedad máxima | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1000 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Upper limit of the humidity setpoint value"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consigna humedad máxima"}}} | [] | modbus
495 | 5310 | MAX_DEMAND | Máxima demanda de energía permitida | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1000 |  |  | 0 | Gec44 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"maximum allowable energy demand - energy meter"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Máxima demanda de energía permitida"}}} | [] | modbus
496 | 5311 | MIN_DEMAND | Mínima demanda de energía permitida - medidor de energía | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1000 |  |  | 0 | Gec44 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Minimum allowable energy demand - energy meter"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Mínima demanda de energía permitida - medidor de energía"}}} | [] | modbus
497 | 5385 | EDV_1.I37_START_EEV_OPENING_RATIO_msk | Porcentaje apertura arranque - Circuito 1 en driver | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 100 | % |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Open valve startup (capacity ratio EVAP / EEV) - circuit 1 "},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Porcentaje apertura arranque - Circuito 1 en driver"}}} | [] | modbus
498 | 5386 | EDV_1.I60_START_EEV_OPEN_RATIO_2ND_msk | Porcentaje apertura arranque - Circuito 2 en driver | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 100 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Open valve startup (capacity ratio EVAP / EEV) - circuit 2 "},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Porcentaje apertura arranque - Circuito 2 en driver"}}} | [] | modbus
499 | 5387 | EDV_1.I38_PID_Ti_msk | PID: Tiempo integración -Circuito 1 en driver | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1000 | s |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"PID: Integral time - circuit 1 from driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"PID: Tiempo integración -Circuito 1 en driver"}}} | [] | modbus
500 | 5388 | EDV_1.I61_PID_Ti_2ND_msk | PID: Tiempo integración - Circuito 2 en driver | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1000 | s |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"PID: integral time -circuit 2 from driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"PID: Tiempo integración - Circuito 2 en driver"}}} | [] | modbus
501 | 5389 | EDV_1.I44_HITCOND_ALARM_DELAY_msk | Retardo alarma temperatura condensación alta -Circuito 1 en | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 18000 | s |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"High condensing temperature alarm delay - circuit 1 from dr"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Retardo alarma temperatura condensación alta -Circuito 1 en"}}} | [] | modbus
502 | 5390 | EDV_1.I43_LOW_SH_ALARM_DELAY_msk | LowSH: Retardo alarma sobrecalentamieno baja - Circuito 1 en | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 18000 | s |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"LowSH: low superheat alarm delay - circuit 1 from driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"LowSH: Retardo alarma sobrecalentamieno baja - Circuito 1 en"}}} | [] | modbus
503 | 5391 | EDV_1.I41_LOP_ALARM_DELAY_msk | LOP: Retardo alarma temperatura evaporación baja - Circuito | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 18000 | s |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"LOP: low evaporation temperature alarm delay -circuit 1 fro"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"LOP: Retardo alarma temperatura evaporación baja - Circuito"}}} | [] | modbus
504 | 5392 | EDV_1.I42_MOP_ALARM_DELAY_msk | MOP: Retardo alarma temperatura evaporación alta - Circuito | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 18000 | s |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"MOP: high temperature evaporation alarm delay - circuit 1 f"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"MOP: Retardo alarma temperatura evaporación alta - Circuito"}}} | [] | modbus
505 | 5393 | EDV_1.I62_LOW_SH_ALARM_DELAY_2ND_msk | LowSH: Retardo alarma sobrecalentamieno baja - Circuito 2 en | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 18000 | s |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"LowSH: low superheat alarm delay -circuit 2 from driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"LowSH: Retardo alarma sobrecalentamieno baja - Circuito 2 en"}}} | [] | modbus
506 | 5394 | EDV_1.I63_LOP_ALARM_DELAY_2ND_msk | LOP: Retardo alarma temperatura evaporación baja - Circuito | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 18000 | s |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"LOP: low evaporation temperature alarm delay - circuit 2 fr"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"LOP: Retardo alarma temperatura evaporación baja - Circuito"}}} | [] | modbus
507 | 5395 | EDV_1.I64_MOP_ALARM_DELAY_2ND_msk | MOP: Retardo alarma temperatura evaporación alta - Circuito | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 18000 | s |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"MOP: high evaporation temperature alarm delay - circuit 2 f"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"MOP: Retardo alarma temperatura evaporación alta - Circuito"}}} | [] | modbus
508 | 5396 | EDV_2.I37_START_EEV_OPENING_RATIO_msk | Apertura inicial arranque - Circuito 1 en driver | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 100 | % |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Open valve startup (capacity ratio EVAP / EEV) - circuit 1 "},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Apertura inicial arranque - Circuito 1 en driver"}}} | [] | modbus
509 | 5397 | EDV_2.I60_START_EEV_OPEN_RATIO_2ND_msk | Apertura inicial arranque - Circuito 2 en driver | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 100 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Open valve startup (capacity ratio EVAP / EEV) - circuit 2 "},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Apertura inicial arranque - Circuito 2 en driver"}}} | [] | modbus
510 | 5400 | Start_EEV_Open_Ratio_CH | Porcentaje apertura VEE en el arranque - Modo frío | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 100 | % |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"% Percentage of VEE opening at start- Cold Mode"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Porcentaje apertura VEE en el arranque - Modo frío"}}} | [] | modbus
511 | 5401 | Start_EEV_Open_Ratio_HP | Porcentaje apertura VEE en el arranque - Modo calor | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 100 | % |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"% Percentage of VEE opening at start - HeatPump mode"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Porcentaje apertura VEE en el arranque - Modo calor"}}} | [] | modbus
512 | 5402 | Start_EEV_Open_Ratio_DF | Porcentaje apertura VEE arranque - Desescarche | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 100 | % |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Startup valve opening % (capacity ratio EVAP / EEV) - Defros"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Porcentaje apertura VEE arranque - Desescarche"}}} | [] | modbus
513 | 5407 | Time_Remaining_Cleaning | Tiempo restante en la renovacion de aire, en calidad de aire | AIR QUALITY |  | simple | 0 | 4 | 0 | 0 | 999 | min |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Remaining Time in Air Renewal, in Air Quality"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Tiempo restante en la renovacion de aire, en calidad de aire"}}} | [] | modbus
514 | 5408 | Hum_THTune_1 | Humedad THTune 1 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1000 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Humidity THTUNE 1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Humedad THTune 1"}}} | [] | modbus
515 | 5409 | EDV_1. I7_SH_UNIT_POWER_PERCENT_msk | Capacidad frigorífica - circuito 1 en driver | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 100 | % |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Cooling capacity - circuit 1 from driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Capacidad frigorífica - circuito 1 en driver"}}} | [] | modbus
516 | 5410 | I50_SH_UNIT_POWER_PERC_2ND_msk | Capacidad frigorífica - circuito 2 en driver | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 100 | % |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Cooling capacity - circuit 2 from driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Capacidad frigorífica - circuito 2 en driver"}}} | [] | modbus
517 | 5413 | CurrSpeed_EBM_Imp | Velocidad actual ventilador impulsión EBM [rpm] | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 32767 | rpm |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Current speed in [rpm] of the fan for Ebmpapst supply fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Velocidad actual ventilador impulsión EBM [rpm]"}}} | [] | modbus
518 | 5414 | AmpOut_EBM_Imp | Intensidad ventilador impulsión EBM | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 | A |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"DC link amperage in [A] for Ebmpapst supply fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Intensidad ventilador impulsión EBM"}}} | [] | modbus
519 | 5415 | Vout_EBM_Imp | Voltaje ventilador impulsión EBM | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 | V |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"DC link voltage for Ebmpapst supply fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Voltaje ventilador impulsión EBM"}}} | [] | modbus
520 | 5416 | ElectrTemp_EBM_Imp | Temperatura circuito interno ventilador impulsión EBM | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 999 | °C |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Internal circuit temperature for Ebmpapst supply fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura circuito interno ventilador impulsión EBM"}}} | [] | modbus
521 | 5417 | CurrSpeed_EBM_Ret | Velocidad actual ventilador retorno EBM [rpm] | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 32767 | rpm |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Current speed in [rpm] of the fan for Ebmpapst return fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Velocidad actual ventilador retorno EBM [rpm]"}}} | [] | modbus
522 | 5418 | AmpOut_EBM_Ret | Corriente ventilador retorno EBM | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 | A |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"DC link amperage in [A] for Ebmpapst return fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Corriente ventilador retorno EBM"}}} | [] | modbus
523 | 5419 | Vout_EBM_Ret | Voltaje ventilador retorno EBM | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 | V |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"DC link voltage for Ebmpapst return fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Voltaje ventilador retorno EBM"}}} | [] | modbus
524 | 5420 | PresionRetorno | Diferencial presión ventilador retorno | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 | Pa |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Pressure differential for return fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Diferencial presión ventilador retorno"}}} | [] | modbus
525 | 5421 | SpeedReq_tmp | Velocidad requerida según control velocidad para ventilador | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1092 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Required Speed in [ 0 - 100.0%] or [rps] according to Speed "},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Velocidad requerida según control velocidad para ventilador"}}} | [] | modbus
526 | 5422 | CurrSpeed_Ret_ZA | Velocidad actual ventilador ZiehlAbegg | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 32767 | rpm |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Actual speed [rpm] of the Zhiel-Abegg fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Velocidad actual ventilador ZiehlAbegg"}}} | [] | modbus
527 | 5423 | PwrConsumption_IR33 | Consumo potencia ventilador Retorno | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 | W |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Return Fan Power Consumption"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consumo potencia ventilador Retorno"}}} | [] | modbus
528 | 5424 | MotA_H | Corriente motor (parte alta cifra numerica) ventilador Retor | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 999 | A |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Motor Current (Upper Numerical Figure) of Return Fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Corriente motor (parte alta cifra numerica) ventilador Retor"}}} | [] | modbus
529 | 5425 | MotA_L | Corriente motor (parte baja cifra numérica) ventilador Retor | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 99 | A |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Return Fan Motor Current (Lower Part numerical frigure)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Corriente motor (parte baja cifra numérica) ventilador Retor"}}} | [] | modbus
530 | 5426 | WorkStatusCode_Ret_ZA | Estado funcionamiento ventilador retorno Zhiel-Abegg | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 16 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Operating Status of Zhiel-Abegg Return Fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Estado funcionamiento ventilador retorno Zhiel-Abegg"}}} | [] | modbus
531 | 5427 | PwrConsumption | Consumo potencia ventilador impulsion Nicotra | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 32767 | W |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Impulsion Nicotra Fan Power Consumption"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Consumo potencia ventilador impulsion Nicotra"}}} | [] | modbus
532 | 5428 | MotAmper | Corriente motor ventilador Impulsion Nicotra | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 999 | A |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Fan Motor Current Impulsion Nicotra"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Corriente motor ventilador Impulsion Nicotra"}}} | [] | modbus
533 | 5429 | CurrSpeed_rpm_2 | Velocidad ventilador [rpm] | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 32767 | rpm |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Actual speed [rpm] of the fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Velocidad ventilador [rpm]"}}} | [] | modbus
534 | 5432 | CurrSpeed_EBM_1 | Velocidad ventilador EBM 1 [rpm] | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 32767 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Current speed in [rpm] of the fan for Ebmpapst fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Velocidad ventilador EBM 1 [rpm]"}}} | [] | modbus
535 | 5433 | PwrOut_EBM_1 | Potencia ventilador EBM 1 [W] | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 32767 | W |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Current power in [W] for Ebmpapst fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Potencia ventilador EBM 1 [W]"}}} | [] | modbus
536 | 5434 | AmpOut_EBM_1 | Corriente ventilador EBM 1 [A] | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 |  |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"DC link amperage in [A] for Ebmpapst fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Corriente ventilador EBM 1 [A]"}}} | [] | modbus
537 | 5435 | Vout_EBM_1 | Voltaje ventilador EBM 1 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 | V |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"DC link voltage for Ebmpapst fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Voltaje ventilador EBM 1"}}} | [] | modbus
538 | 5436 | ElectrTemp_EBM_1 | Temperatura circuito interno ventilador EBM 1 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 999 | °C |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Internal circuit temperature for Ebmpapst fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura circuito interno ventilador EBM 1"}}} | [] | modbus
539 | 5437 | WarningCode_EBM_1 | Warning ventilador EBM 1 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 16 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Warning code for Ebmpaps fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Warning ventilador EBM 1"}}} | [] | modbus
540 | 5438 | CurrSpeed_EBM_2 | Velocidad ventilador EBM circuito 2 [rpm] | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 32767 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Current speed in [rpm] of the fan for Ebmpapst fan Circuit 2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Velocidad ventilador EBM circuito 2 [rpm]"}}} | [] | modbus
541 | 5439 | PwrOut_EBM_2 | Potencia ventilador EBM 2 [W] | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 32767 | W |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Current power in [W] for Ebmpapst fan circuit 2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Potencia ventilador EBM 2 [W]"}}} | [] | modbus
542 | 5440 | AmpOut_EBM_2 | Corriente ventilador EBM circuito 2 [A] | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 |  |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"DC link amperage in [A] for Ebmpapst fan circuit 2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Corriente ventilador EBM circuito 2 [A]"}}} | [] | modbus
543 | 5441 | Vout_EBM_2 | Voltaje ventilador EBM circuito 2 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 | V |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"DC link voltage for Ebmpapst fan circuit 2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Voltaje ventilador EBM circuito 2"}}} | [] | modbus
544 | 5442 | ElectrTemp_EBM_2 | Temperatura circuito interno ventilador EBM circuito 2 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 999 | °C |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Internal circuit temperature for Ebmpapst fan circuit 2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura circuito interno ventilador EBM circuito 2"}}} | [] | modbus
545 | 5443 | WarningCode_EBM_2 | Warning ventilador EBM circuito 2 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 16 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Warning code for Ebmpaps fan circuit 2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Warning ventilador EBM circuito 2"}}} | [] | modbus
546 | 5444 | AlrmCode_EBM_2 | Código alarma ventilador EBM circuito 2 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 16 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Alarm code for Ebmpaps fan circuit 2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Código alarma ventilador EBM circuito 2"}}} | [] | modbus
547 | 5445 | AlrmCode_EBM_1 | Código alarma ventilador EBM circuito 1 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 16 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Alarm code for Ebmpaps fan circuit 1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Código alarma ventilador EBM circuito 1"}}} | [] | modbus
548 | 5446 | CurrSpeed_EBM_3 | Velocidad ventilador EBM circuito 3 [rpm] | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 32767 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Current speed in [rpm] of the fan for Ebmpapst fan circuit 3"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Velocidad ventilador EBM circuito 3 [rpm]"}}} | [] | modbus
549 | 5447 | PwrOut_EBM_3 | Potencia ventilador EBM circuito 3 [W] | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 32767 | W |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Current power in [W] for Ebmpapst fan circuit 3"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Potencia ventilador EBM circuito 3 [W]"}}} | [] | modbus
550 | 5448 | AmpOut_EBM_3 | Corriente ventilador EBM circuito 3 [A] | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 |  |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"DC link amperage in [A] for Ebmpapst fan circuit 3"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Corriente ventilador EBM circuito 3 [A]"}}} | [] | modbus
551 | 5449 | Vout_EBM_3 | Voltaje ventilador EBM circuito 3 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | -32768 | 32767 | V |  | 0 |  | 0 | s16 |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"DC link voltage for Ebmpapst fan circuit 3"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Voltaje ventilador EBM circuito 3"}}} | [] | modbus
552 | 5450 | ElectrTemp_EBM_3 | Temperatura circuito interno ventilador EBM circuito 3 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 999 | °C |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Internal circuit temperature for Ebmpapst fan circuit 3"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Temperatura circuito interno ventilador EBM circuito 3"}}} | [] | modbus
553 | 5451 | WarningCode_EBM_3 | Warning ventilador EBM circuito 3 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 16 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Warning code for Ebmpaps fan circuit 3"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Warning ventilador EBM circuito 3"}}} | [] | modbus
554 | 5452 | AlrmCode_EBM_3 | Código alarma ventilador EBM circuito 3 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 16 |  |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Alarm code for Ebmpaps fan circuit 3"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Código alarma ventilador EBM circuito 3"}}} | [] | modbus
555 | 5453 | EDV_2.I7_SH_UNIT_POWER_PERCENT | Capacidad frigorífica - Circuito 1 en placa | PARAMETERS |  | simple | 0 | 3 | 6 | 0 | 100 | % |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Cooling capacity - circuit 1 on board"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Capacidad frigorífica - Circuito 1 en placa"}}} | [] | modbus
556 | 5454 | EDV_2.I50_SH_UNIT_POWER_PERCENT_2ND | Capacidad frigorífica - Circuito 2 en plca | PARAMETERS |  | simple | 0 | 3 | 6 | 0 | 100 | % |  | 0 |  | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Cooling capacity - circuit 2 on board"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Capacidad frigorífica - Circuito 2 en plca"}}} | [] | modbus
557 | 1 | GLOBAL_ALARM | Alarma General | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Global (general) alarm"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma General"}}} | [] | modbus
558 | 2 | RESET_BMS | Reset Alarma Por Modbus | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Alarms reset by Modbus supervisor"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Reset Alarma Por Modbus"}}} | [] | modbus
559 | 3 | ON_LINE | Estado Supervisión (1=Online) | SYSTEM |  | simple | 0 | 3 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Status of the supervisory system (1=supervisory system onlin"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Estado Supervisión (1=Online)"}}} | ["library_identifier"] | modbus
560 | 4 | ID_AL_KL_VENT_INT | Alarma Klixon Ventilador Interior / Paro Ext. Inmediato | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Klixon alarm internal fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma Klixon Ventilador Interior / Paro Ext. Inmediato"}}} | [] | modbus
561 | 5 | SysOn | Estado Unidad (1: unidad On/ 0: unidad Off) | STATUS |  | basic | 60 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Unit status (1- Unit On/0- Unit Off)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Estado Unidad (1: unidad On/ 0: unidad Off)"}}} | [] | modbus
562 | 6 | COMPRESOR1_CIRC1 | Compresor 1 Circuito 1 (0-No habilitado ; 1- Habilitado) | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Compressor 1 circuit 1 (0 - Not enable; 1- Enable)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Compresor 1 Circuito 1 (0-No habilitado ; 1- Habilitado)"}}} | [] | modbus
563 | 7 | COMPRESOR2_CIRC1 | Compresor 2 Circuito 1 (0-No habilitado ; 1- Habilitado) | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Compressor 2 circuit 1 (0 - Not enable; 1- Enable)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Compresor 2 Circuito 1 (0-No habilitado ; 1- Habilitado)"}}} | [] | modbus
564 | 8 | COMPRESOR1_CIRC2 | Compresor 1 Circuito 2 (0-No habilitado ; 1- Habilitado) | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Compressor 1 circuit 2 (0 - Not enable; 1- Enable)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Compresor 1 Circuito 2 (0-No habilitado ; 1- Habilitado)"}}} | [] | modbus
565 | 9 | COMPRESOR2_CIRC2 | Compresor 2 Circuito 2 (0-No habilitado ; 1- Habilitado) | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Compressor 2 circuit 2 (0 - Not enable; 1- Enable)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Compresor 2 Circuito 2 (0-No habilitado ; 1- Habilitado)"}}} | [] | modbus
566 | 10 | VENT_INTERIOR | Estado Ventilador Interior | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Supply fan status"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Estado Ventilador Interior"}}} | [] | modbus
567 | 11 | INV_VER | Estado Invierno/ Verano (0-Invierno; 1- Verano | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Cooling / Heating status (0-Cooling; 1-Heating)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Estado Invierno/ Verano (0-Invierno; 1- Verano"}}} | [] | modbus
568 | 12 | COMPRESOR1_CIRC3 | Compresor 1 Circuito 3 (0-No habilitado ; 1- Habilitado) | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Compressor 1 circuit 3 (0 - Not enable; 1- Enable)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Compresor 1 Circuito 3 (0-No habilitado ; 1- Habilitado)"}}} | [] | modbus
569 | 13 | COMPRESOR2_CIRC3 | Compresor 2 Circuito 3 (0-No habilitado ; 1- Habilitado) | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Compressor 2 circuit 3 (0 - Not enable; 1- Enable)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Compresor 2 Circuito 3 (0-No habilitado ; 1- Habilitado)"}}} | [] | modbus
570 | 14 | COMPRESOR1_CIRC_REC | Compresor 1 Circuito Recuperación (0-No habilitado ; 1- Hab | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Compressor 1 recovery circuit (0 - Not enable; 1- Enable)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Compresor 1 Circuito Recuperación (0-No habilitado ; 1- Hab"}}} | [] | modbus
571 | 15 | En_FRIO_CALOR_Auto | Habilitado Cambio Calor / Frío Automatico | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Enable automatic cooling / heating"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Habilitado Cambio Calor / Frío Automatico"}}} | [] | modbus
572 | 16 | INV_VER_X_PANT | Cambio Invierno / Verano | SERVICES |  | simple | 0 | 3 | 6 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Cooling / Heating display"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Cambio Invierno / Verano"}}} | [] | modbus
573 | 17 | LIMITE1 | Primer Limite De Potencia, limitacion de la demanda circuito | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Power limit 1, demand limitationcircuits with 1 to 6 compres"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Primer Limite De Potencia, limitacion de la demanda circuito"}}} | [] | modbus
574 | 18 | LIMITE2 | Segundo Limite De Potencia, limitacion de la demanda circuit | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Power limit 2, demand limitation circuits with 1 to 6 compre"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Segundo Limite De Potencia, limitacion de la demanda circuit"}}} | [] | modbus
575 | 19 | LIMITE3 | Tercer Limite De Potencia, limitacion de la demanda circuito | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Power limit 3, demand limitation circuits with 1 to 6 compre"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Tercer Limite De Potencia, limitacion de la demanda circuito"}}} | [] | modbus
576 | 20 | LIMITE4 | Cuarto Limite De Potencia, limitacion de la demanda circuito | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Power limit 4, demand limitation circuits with 1 to 6 compre"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Cuarto Limite De Potencia, limitacion de la demanda circuito"}}} | [] | modbus
577 | 21 | LIMITE5 | Quinto Limite De Potencia ,limitacion de la demanda, circuit | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Power limit 5, demand limitation circuits with 1 to 6 compre"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Quinto Limite De Potencia ,limitacion de la demanda, circuit"}}} | [] | modbus
578 | 22 | LIMITE6 | Sexto Limite De Potencia, limitacion de la demanda circuitos | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Power limit 6, demand limitation circuits with 1 to 6 compre"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Sexto Limite De Potencia, limitacion de la demanda circuitos"}}} | [] | modbus
579 | 23 | En_Dig_In_OnOff | Habilita Entrada Remoto On / Off | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Enable On-Off unit by digital input"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Habilita Entrada Remoto On / Off"}}} | [] | modbus
580 | 24 | ID_AL_PRESOST_ALTA_DESC_CIRC1 | Alarma Presostato De Alta C1 (0-No alarma; 1-Alarma) | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"High pressure pressostat alarm circuit 1 (0-No alarm; 1-Alar"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma Presostato De Alta C1 (0-No alarma; 1-Alarma)"}}} | [] | modbus
581 | 25 | ID_AL_PRESOST_BAJA_CIRC1 | Alarma Presostato De Baja C1 (0-No alarma; 1-Alarma) | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Low pressure pressostat alarm circuit 1 (0-No alarm; 1-Alarm"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma Presostato De Baja C1 (0-No alarma; 1-Alarma)"}}} | [] | modbus
582 | 26 | mID_AL_TERMICOS_CIRC1 | Termicos Compresores Del Circuito 1 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Compressors Overload Compressors Circ1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Termicos Compresores Del Circuito 1"}}} | [] | modbus
583 | 27 | COMPRESOR3_CIRC1 | Compresor 3 Circuito 1 (0-No habilitado ; 1- Habilitado) | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Compressor 3 circuit 1 (0 - Not enable; 1- Enable)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Compresor 3 Circuito 1 (0-No habilitado ; 1- Habilitado)"}}} | [] | modbus
584 | 28 | ID_AL_PRESOST_ALTA_DESC_CIRC2 | Alarma Presostato De Alta C2 (0-No alarma; 1-Alarma) | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"High pressure pressostat alarm circuit 2 (0-No alarm; 1-Alar"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma Presostato De Alta C2 (0-No alarma; 1-Alarma)"}}} | [] | modbus
585 | 29 | ID_AL_PRESOST_BAJA_CIRC2 | Alarma Presostato De Baja C2 (0-No alarma; 1-Alarma) | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Low pressure pressostat alarm circuit 2 (0-No alarm; 1-Alarm"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma Presostato De Baja C2 (0-No alarma; 1-Alarma)"}}} | [] | modbus
586 | 30 | mID_AL_TERMICOS_CIRC2 | Termicos Compresores Del Circuito 2 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Compressors Overload Compressors Circ2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Termicos Compresores Del Circuito 2"}}} | [] | modbus
587 | 31 | COMPRESOR3_CIRC2 | Compresor 3 Circuito 2 (0-No alarma; 1-Alarma) | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Compressor 3 circuit 2 (0 - Not enable; 1- Enable)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Compresor 3 Circuito 2 (0-No alarma; 1-Alarma)"}}} | [] | modbus
588 | 32 | ID_AL_PRESOST_ALTA_DESC_CIRC3 | Alarma Presostato De Alta C3 (0-No alarma; 1-Alarma) | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"High pressure pressostat alarm circuit 3 (0-No alarm; 1-Alar"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma Presostato De Alta C3 (0-No alarma; 1-Alarma)"}}} | [] | modbus
589 | 33 | ID_AL_PRESOST_BAJA_CIRC3 | Alarma Presostato De Baja C3 (0-No alarma; 1-Alarma) | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Low pressure pressostat alarm circuit 3 (0-No alarm; 1-Alarm"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma Presostato De Baja C3 (0-No alarma; 1-Alarma)"}}} | [] | modbus
590 | 34 | mID_AL_TERMICOS_CIRC3 | Termicos Compresores Del Circuito 3 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Compressors Overload Compressors Circ3"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Termicos Compresores Del Circuito 3"}}} | [] | modbus
591 | 35 | COMPRESOR3_CIRC3 | Compresor 3 Circuito 3 (0-No habilitado ; 1- Habilitado) | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Compressor 3 circuit 3 (0 - Not enable; 1- Enable)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Compresor 3 Circuito 3 (0-No habilitado ; 1- Habilitado)"}}} | [] | modbus
592 | 36 | ID_AL_QUEMA_RESIST | Alarma Quemador / Resistencia (Caudal/Termistores) | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Elect.Heater/Burner alarm"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma Quemador / Resistencia (Caudal/Termistores)"}}} | [] | modbus
593 | 37 | ID_AL_PRESOST_ALTA_DESC_CIRC_REC | Alarma Presostato De Alta Circ. Recuperación / Klixon Ventil | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Recovery circuit high pressure pressostat alarm"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma Presostato De Alta Circ. Recuperación / Klixon Ventil"}}} | [] | modbus
594 | 38 | ID_AL_PRESOST_BAJA_CIRC_REC | Estado Alarma Presostato De Baja Circ. Recuperación (0-No al | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Recovery circuit low pressure pressostat alarm (0-No alarm; "},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Estado Alarma Presostato De Baja Circ. Recuperación (0-No al"}}} | [] | modbus
595 | 39 | ID_AL_TERMICO_COMPRE1_CIRC_REC | Estado Alarma Térmico Compresor 1 Circ. Recuperación (0-No a | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Recovery circuit overload compressor 1 alarm (0-No alarm; 1-"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Estado Alarma Térmico Compresor 1 Circ. Recuperación (0-No a"}}} | [] | modbus
596 | 40 | ACT_DESC_CIRC1 | Estado Desescarche C1 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Defrost circuit 1 status"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Estado Desescarche C1"}}} | [] | modbus
597 | 41 | ACT_DESC_CIRC2 | Estado Desescarche C2 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Defrost circuit 2 status"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Estado Desescarche C2"}}} | [] | modbus
598 | 42 | ACT_DESC_CIRC3 | Estado Desescarche C3 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Defrost circuit 3 status"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Estado Desescarche C3"}}} | [] | modbus
599 | 43 | Superv_OnOff | On-Off Por Supervisor | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"On-Off supervision"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"On-Off Por Supervisor"}}} | [] | modbus
600 | 45 | Al_Present_EBM_Imp | Alarma Ventilador Impulsión Ebm | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Supply fan EBM alarm"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma Ventilador Impulsión Ebm"}}} | [] | modbus
601 | 46 | ID_AL_ANTIFREEZE_COIL | Alarma Anti-hielo de bateria (0-No alarma; 1-Alarma) | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Battery anti-freeze alarm"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma Anti-hielo de bateria (0-No alarma; 1-Alarma)"}}} | [] | modbus
602 | 47 | ONLY_COOLING | Solo Verano | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Cooling"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Solo Verano"}}} | [] | modbus
603 | 48 | ONLY_HEATING | Solo Invierno | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Heating"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Solo Invierno"}}} | [] | modbus
604 | 49 | COOLING_HEATING | Invierno/Verano | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Cooling/Heating"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Invierno/Verano"}}} | [] | modbus
605 | 50 | Write_Data | Grabar Horarios, permite guardar el horario indicado en prog | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Save Schedules, allows you to save the time indicated in the"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Grabar Horarios, permite guardar el horario indicado en prog"}}} | [] | modbus
606 | 51 | VALV_INVERSION_CICLO_CIRC1 | Válvula Inversión Ciclo Circuito 1 0=Calor / 1=Frio | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Cycle inverter valve circuit 1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Válvula Inversión Ciclo Circuito 1 0=Calor / 1=Frio"}}} | [] | modbus
607 | 52 | VALV_INVERSION_CICLO_CIRC2 | Válvula Inversión Ciclo Circuito 2 0=Calor / 1=Frio | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Cycle inverter valve circuit 2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Válvula Inversión Ciclo Circuito 2 0=Calor / 1=Frio"}}} | [] | modbus
608 | 53 | VALV_INVERSION_CICLO_CIRC3 | Válvula Inversión Ciclo Circuito 3 0=Calor / 1=Frio | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Cycle inverter valve circuit 3"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Válvula Inversión Ciclo Circuito 3 0=Calor / 1=Frio"}}} | [] | modbus
609 | 54 | ETAPA1_QUEMA_RESIS | Etapa 1 Quemador / Resistencia | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Elect.Heater/Burner stage 1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Etapa 1 Quemador / Resistencia"}}} | [] | modbus
610 | 55 | ETAPA2_QUEMA_RESIS | Etapa 2 Quemador / Resistencia | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Elect.Heater/Burner stage 2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Etapa 2 Quemador / Resistencia"}}} | [] | modbus
611 | 56 | HUMIDIFICADOR | Humidificador | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Humidifier"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Humidificador"}}} | [] | modbus
612 | 57 | VENT_EXT_CIRC1_ESTRELLA | Ventilador Exterior Circuito 1 Estrella | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"External fan circuit 1 star"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Ventilador Exterior Circuito 1 Estrella"}}} | [] | modbus
613 | 58 | VENT_EXT_CIRC1_TRIANGULO | Ventilador Exterior Circuito 1 Triangulo | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"External fan circuit 1 delta"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Ventilador Exterior Circuito 1 Triangulo"}}} | [] | modbus
614 | 59 | VENT_EXT_CIRC2_ESTRELLA | Ventilador Exterior Circuito 2 Estrella | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"External fan circuit 2 star"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Ventilador Exterior Circuito 2 Estrella"}}} | [] | modbus
615 | 60 | VENT_EXT_CIRC2_TRIANGULO | Ventilador Exterior Circuito 2 Triangulo | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"External fan circuit 2 delta"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Ventilador Exterior Circuito 2 Triangulo"}}} | [] | modbus
616 | 61 | VENT_EXT_CIRC3_ESTRELLA | Ventilador Exterior Circuito 3 Estrella | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"External fan circuit 3 star"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Ventilador Exterior Circuito 3 Estrella"}}} | [] | modbus
617 | 62 | VENT_EXT_CIRC3_TRIANGULO | Ventilador Exterior Circuito 3 Triangulo | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"External fan circuit 3 delta"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Ventilador Exterior Circuito 3 Triangulo"}}} | [] | modbus
618 | 65 | mAL_CONT | Alarmas Horas Funcionamiento Comp1 Circ1 | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Working hours comp1 circ1 alarms"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarmas Horas Funcionamiento Comp1 Circ1"}}} | [] | modbus
619 | 66 | mAL_CONT_2 | Alarmas Horas Funcionamiento Comp1 Circ2 | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Working hours comp1 circ2 alarms"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarmas Horas Funcionamiento Comp1 Circ2"}}} | [] | modbus
620 | 67 | mAL_CONT_3 | Alarmas Horas Funcionamiento Comp3 Circ1 | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Working hours comp3 circ1 alarms"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarmas Horas Funcionamiento Comp3 Circ1"}}} | [] | modbus
621 | 68 | mAL_CONT_4 | Alarmas Horas Funcionamiento Comp2 Circ2 | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Working hours comp2 circ2 alarms"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarmas Horas Funcionamiento Comp2 Circ2"}}} | [] | modbus
622 | 69 | mAL_CONT_5 | Alarmas Horas Funcionamiento Comp1 Circ3 | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Working hours comp1 circ3 alarms"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarmas Horas Funcionamiento Comp1 Circ3"}}} | [] | modbus
623 | 70 | mAL_CONT_6 | Alarmas Horas Funcionamiento Comp2 Circ3 | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Working hours comp2 circ3 alarms"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarmas Horas Funcionamiento Comp2 Circ3"}}} | [] | modbus
624 | 71 | mAL_CONT_7 | Alarmas Horas Funcionamiento Comp1 Circ3 | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Working hours comp1 circ3 alarms"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarmas Horas Funcionamiento Comp1 Circ3"}}} | [] | modbus
625 | 72 | Gen_High_Pressure_Circ1 | Alta Presión Presostato Circ1 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"High pressure pressostat circ1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alta Presión Presostato Circ1"}}} | [] | modbus
626 | 73 | Gen_High_Pressure_Circ2 | Alta Presión Presostato Circ2 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"High pressure pressostat circ2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alta Presión Presostato Circ2"}}} | [] | modbus
627 | 74 | Gen_High_Pressure_Circ3 | Alta Presión Presostato Circ3 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"High pressure pressostat circ3"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alta Presión Presostato Circ3"}}} | [] | modbus
628 | 75 | Gen_High_Pressure_Circ_REC | Alta Presión Presostato Circ Recuperación | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"High pressure pressostat recovery circuit"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alta Presión Presostato Circ Recuperación"}}} | [] | modbus
629 | 76 | Gen_Low_Pressure_Circ1 | Baja Presión Presostato Circ1 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Low pressure pressostat circ1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Baja Presión Presostato Circ1"}}} | [] | modbus
630 | 77 | Gen_Low_Pressure_Circ2 | Baja Presión Presostato Circ2 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Low pressure pressostat circ2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Baja Presión Presostato Circ2"}}} | [] | modbus
631 | 78 | Gen_Low_Pressure_Circ3 | Baja Presión Presostato Circ3 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Low pressure pressostat circ3"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Baja Presión Presostato Circ3"}}} | [] | modbus
632 | 79 | Gen_Low_Pressure_Circ_REC | Baja Presión Presostato Circ Recuperación | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Low pressure pressostat recovery circuit"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Baja Presión Presostato Circ Recuperación"}}} | [] | modbus
633 | 80 | FreeCool_Active | Freecooling Activo | DAMPERS |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Freecooling active"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Freecooling Activo"}}} | [] | modbus
634 | 81 | FreeHeat_Active | Freeheating Activo | DAMPERS |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Freeheating active"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Freeheating Activo"}}} | [] | modbus
635 | 82 | EN_SCHEDULE_ON_OFF | Horario On Off | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"On-Off schedule"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Horario On Off"}}} | [] | modbus
636 | 83 | ACT_FASES_PCO | Activar Fases Pco | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"PCO phases activation"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Activar Fases Pco"}}} | [] | modbus
637 | 84 | Comp1_Circ1 | Estado Compresor1 circuito1 (0: Off; 1: On) si este se encue | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Compressor1 circuit1 (0: Off; 1: On)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Estado Compresor1 circuito1 (0: Off; 1: On) si este se encue"}}} | [] | modbus
638 | 85 | Comp2_Circ1 | Estado Compresor2 circuito1 (0: Off; 1: On) si este se encue | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Compressor2 circuit1 (0: Off; 1: On)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Estado Compresor2 circuito1 (0: Off; 1: On) si este se encue"}}} | [] | modbus
639 | 86 | Comp3_Circ1 | Estado Compresor3 circuito1 (0: Off; 1: On) si este se encue | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Compressor3 circuit1 (0: Off; 1: On)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Estado Compresor3 circuito1 (0: Off; 1: On) si este se encue"}}} | [] | modbus
640 | 87 | Al_Probe03 | Alarma sonda Temperatura Mezcla (0-No alarma; 1-Alarma) | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Mixing temperature probe Alarm"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma sonda Temperatura Mezcla (0-No alarma; 1-Alarma)"}}} | [] | modbus
641 | 88 | Al_Probe12 | Alarma Humedad Interior | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Internal humidity"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma Humedad Interior"}}} | [] | modbus
642 | 89 | Al_Probe05 | Alarma Humedad Exterior | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"External humidity"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma Humedad Exterior"}}} | [] | modbus
643 | 91 | ACT_FREE_COOLING_PANT | Freecooling Activo | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Active freecooling"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Freecooling Activo"}}} | [] | modbus
644 | 92 | ACT_FREE_HEATING_PANT | Freeheating Activo | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Active freeheating"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Freeheating Activo"}}} | [] | modbus
645 | 93 | En_Day_Sch_1 | Activar Campos Dia Programado 1 | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Enable all the fields for day scheduler 1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Activar Campos Dia Programado 1"}}} | [] | modbus
646 | 94 | En_Day_Sch_2 | Activar Campos Dia Programado 2 | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Enable all the fields for day scheduler 2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Activar Campos Dia Programado 2"}}} | [] | modbus
647 | 96 | ID_AL_RECUP_ROT | Recuperador Rotativo Alarma | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Rotaty recovery alarm"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Recuperador Rotativo Alarma"}}} | [] | modbus
648 | 97 | Al_Probe01 | Alarma sonda Temperatura Exterior (0-No alarma 1-Alarma) | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"External temperature Probe Alarm (0-No alarm 1-Alarm)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma sonda Temperatura Exterior (0-No alarma 1-Alarma)"}}} | [] | modbus
649 | 98 | Al_Probe02 | Alarma sonda Temperatura Retorno / Ambiente (0-No alarma 1- | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Return / Ambient temperature Probe Alarm (0-No alarm 1-Alar"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma sonda Temperatura Retorno / Ambiente (0-No alarma 1-"}}} | [] | modbus
650 | 99 | Al_Probe04 | Alarma Sonda Temperatura Impulsión (0-No alarma 1-Alarma) | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Supply temperature probe Alarm (0-No alarm 1-Alarm)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma Sonda Temperatura Impulsión (0-No alarma 1-Alarma)"}}} | [] | modbus
651 | 100 | Al_Probe06 | Alarma Sonda Presión Condensación Circuito 1 (0-No alarma 1 | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Condensation pressure circuit 1 probe Alarm (0-No alarm ;1-"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma Sonda Presión Condensación Circuito 1 (0-No alarma 1"}}} | [] | modbus
652 | 104 | RESET_CONT_H | Reinicio contador de Horas de funcionamiento (1 - SI; 0 - No | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Reset Operating Hours counter (1 - YES; 0 - NO)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Reinicio contador de Horas de funcionamiento (1 - SI; 0 - No"}}} | [] | modbus
653 | 105 | AL_CONT | Alarmas superado limite de Horas Funcionamiento (0-No alarma | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Alarms exceeded operating hours (0-No alarm; 1- Alarm)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarmas superado limite de Horas Funcionamiento (0-No alarma"}}} | [] | modbus
654 | 106 | FE_VIDA | Indica correcta comunicación entre Maestro y esclavo, si la | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Indicates correct communication between master and slave, if"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Indica correcta comunicación entre Maestro y esclavo, si la"}}} | [] | modbus
655 | 107 | INV_VER_GLOBAL | Estado Invierno / Verano Desde Maestro Rotacion (Cuando tene | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Cooling / Heating status rotation (Cuando tenemos una Maest"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Estado Invierno / Verano Desde Maestro Rotacion (Cuando tene"}}} | [] | modbus
656 | 108 | PM_GLOBAL | Paro / Marcha Desde Maestra De Rotación (Cuando tenemos una | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Paro / marcha desde maestra de rotación (Cuando tenemos una"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Paro / Marcha Desde Maestra De Rotación (Cuando tenemos una"}}} | [] | modbus
657 | 109 | AL_TERM_VENT_INTERIOR | Alarma Termico Ventilador Interior | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Compressor overload internal fan alarm"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma Termico Ventilador Interior"}}} | [] | modbus
658 | 110 | Al_Est_Grave_Vent_Interior | Alarma Estado Grave Ventilador Interior | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Internal fan serious status alarm"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma Estado Grave Ventilador Interior"}}} | [] | modbus
659 | 111 | Al_Est_Vent_Interior | Alarma Estado Ventilador Interior | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Internal fan status alarm"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma Estado Ventilador Interior"}}} | [] | modbus
660 | 112 | mID_AL_HUMO | Memoria de la alarma por detector de Humo/Fuego (0-No alarma | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Smoke/Fire detector alarm memory (0-No alarm; 1- Alarm)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Memoria de la alarma por detector de Humo/Fuego (0-No alarma"}}} | [] | modbus
661 | 113 | AlrmPresent_EBM_Imp | Alarma Ventilador Ebm de impulsión (0-No alarma; 1- Alarma) | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Supply Ebm Fan Alarm (0-No Alarm; 1- Alarm)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma Ventilador Ebm de impulsión (0-No alarma; 1- Alarma)"}}} | [] | modbus
662 | 114 | Al_Offline_EBM_Imp | Alarma Ventilador impulsión offline EBM (0-No alarma; 1- Ala | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Suply Fan offline alarm EBM (0-No alarm; 1- Alarm)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma Ventilador impulsión offline EBM (0-No alarma; 1- Ala"}}} | [] | modbus
663 | 115 | Al_Present_EBM_Ret | Alarma Ventilador Retorno Ebm (0-No alarma; 1- Alarma) | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"EBM return fan alarm (0-No alarm; 1- Alarm)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma Ventilador Retorno Ebm (0-No alarma; 1- Alarma)"}}} | [] | modbus
664 | 116 | Al_Offline_EBM_Ret | Alarma Ventilador Retorno Ebm offline (0-No alarma; 1- Alar | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Ebm return fan alarm offline (0-No alarm; 1-Alarm)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma Ventilador Retorno Ebm offline (0-No alarma; 1- Alar"}}} | [] | modbus
665 | 117 | mID_AL_INUNDACION | Estado Entrada Booleana (0:Contacto Cerrado, 1:Abierto) Inun | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Status of the Boolean input (0: contact closed, 1: contact o"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Estado Entrada Booleana (0:Contacto Cerrado, 1:Abierto) Inun"}}} | [] | modbus
666 | 118 | Alrm_Caudal_Int | Falta Caudal Ventilador Interior | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Air flow supply lack"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Falta Caudal Ventilador Interior"}}} | [] | modbus
667 | 119 | Comp3_Circ2 | Estado Compresor3 circuito2 (0: Off; 1: On) si este se enc | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Compressor3 circuit2 (0: Off; 1: On)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Estado Compresor3 circuito2 (0: Off; 1: On) si este se enc"}}} | [] | modbus
668 | 120 | Comp2_Circ2 | Estado Compresor2 circuito2 (0: Off; 1: On) si este se encu | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Compressor2 circuit2 (0: Off; 1: On)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Estado Compresor2 circuito2 (0: Off; 1: On) si este se encu"}}} | [] | modbus
669 | 121 | Alrm_Caudal_Ret | Falta Caudal Ventilador Retorno | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Air flow return lack"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Falta Caudal Ventilador Retorno"}}} | [] | modbus
670 | 122 | AVISO_Tmecla_BAJA_PARO_COMPRE | Aviso Temperatura Mezcla Baja Bloqueo Funcionamiento Compres | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Compressors working block low mixing temperature warning"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Aviso Temperatura Mezcla Baja Bloqueo Funcionamiento Compres"}}} | [] | modbus
671 | 123 | mAL_CONT_8 | Alarmas Horas Funcionamiento Comp3 Circ1 | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Working hours comp3 circ1 alarms"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarmas Horas Funcionamiento Comp3 Circ1"}}} | [] | modbus
672 | 124 | mAL_CONT_9 | Alarmas Horas Funcionamiento Comp3 Circ2 | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Working hours comp3 circ2 alarms"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarmas Horas Funcionamiento Comp3 Circ2"}}} | [] | modbus
673 | 126 | LIMITE7 | Séptimo Limite De Potencia, limitacion de la demanda circuit | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Power limit 7"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Séptimo Limite De Potencia, limitacion de la demanda circuit"}}} | [] | modbus
674 | 127 | LIMITE8 | Octavo Limite De Potencia limitacion de la demanda circuito | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Power limit 8"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Octavo Limite De Potencia limitacion de la demanda circuito"}}} | [] | modbus
675 | 128 | LIMITE9 | Noveno Limite De Potencia limitacion de la demanda circuito | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Power limit 9"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Noveno Limite De Potencia limitacion de la demanda circuito"}}} | [] | modbus
676 | 129 | mID_AL_TERMICO_COMPRE1_CIRC_REC | Alarma Térmico Compresor 1 Circ. Recuperación | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Compressor overload comp1 recovery circuit alarm"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma Térmico Compresor 1 Circ. Recuperación"}}} | [] | modbus
677 | 130 | mAl_HP_Pressostat_Circ1 | Memoria Alarma Presostato De Alta Condensación Circuito 1 | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"High pressure pressostat memory alarm circuit 1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Memoria Alarma Presostato De Alta Condensación Circuito 1"}}} | [] | modbus
678 | 131 | mAl_HP_Pressostat_Circ2 | Memoria Alarma Presostato De Alta Condensación Circuito 2 | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"High pressure pressostat memory alarm circuit 2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Memoria Alarma Presostato De Alta Condensación Circuito 2"}}} | [] | modbus
679 | 132 | mAl_HP_Pressostat_Circ3 | Memoria Alarma Presostato De Alta Condensación Circuito 3 | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"High pressure pressostat memory alarm circuit 3"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Memoria Alarma Presostato De Alta Condensación Circuito 3"}}} | [] | modbus
680 | 133 | mAl_HP_Pressostat_Circ_REC | Memoria Alarma Presostato De Alta Condensación Circuito Recu | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"High pressure pressostat memory alarm recovery circuit"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Memoria Alarma Presostato De Alta Condensación Circuito Recu"}}} | [] | modbus
681 | 134 | mAl_HP_Transducer_Circ1 | Memoria Alarma Presión Condensación Alta Circuito 1 | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"High condensation pressure memory alarm circuit 1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Memoria Alarma Presión Condensación Alta Circuito 1"}}} | [] | modbus
682 | 135 | mAl_HP_Transducer_Circ2 | Memoria Alarma Presión Condensación Alta Circuito 2 | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"High condensation pressure memory alarm circuit 2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Memoria Alarma Presión Condensación Alta Circuito 2"}}} | [] | modbus
683 | 136 | mAl_HP_Transducer_Circ3 | Memoria Alarma Presión Condensación Alta Circuito 3 | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"High condensation pressure memory alarm circuit 3"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Memoria Alarma Presión Condensación Alta Circuito 3"}}} | [] | modbus
684 | 137 | mAl_HP_Transducer_Circ_REC | Memoria Alarma Presión Condensación Alta Circuito Recuperaci | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"High condensation pressure memory alarm recovery circuit"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Memoria Alarma Presión Condensación Alta Circuito Recuperaci"}}} | [] | modbus
685 | 138 | Gen_LP_Pressostat_Circ1 | Alarma Baja Presión Por Presostato Circ1 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"LP by pressostat alarm circ1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma Baja Presión Por Presostato Circ1"}}} | [] | modbus
686 | 139 | Gen_LP_Pressostat_Circ2 | Alarma Baja Presión Por Presostato Circ2 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"LP by pressostat alarm circ2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma Baja Presión Por Presostato Circ2"}}} | [] | modbus
687 | 140 | Gen_LP_Pressostat_Circ3 | Alarma Baja Presión Por Presostato Circ3 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"LP by pressostat alarm circ3"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma Baja Presión Por Presostato Circ3"}}} | [] | modbus
688 | 141 | Gen_LP_Pressostat_Circ_REC | Alarma Baja Presión Por Presostato Circ Recup. | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"LP by pressostat alarm recovery circuit"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma Baja Presión Por Presostato Circ Recup."}}} | [] | modbus
689 | 142 | Gen_LP_Transducer_Circ1 | Alarma Baja Presión Por Transductor Circ1 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"LP by transducer alarm circ1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma Baja Presión Por Transductor Circ1"}}} | [] | modbus
690 | 143 | Gen_LP_Transducer_Circ2 | Alarma Baja Presión Por Transductor Circ2 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"LP by transducer alarm circ2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma Baja Presión Por Transductor Circ2"}}} | [] | modbus
691 | 144 | Gen_LP_Transducer_Circ3 | Alarma Baja Presión Por Transductor Circ3 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"LP by transducer alarm circ3"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma Baja Presión Por Transductor Circ3"}}} | [] | modbus
692 | 145 | Gen_LP_Transducer_Circ_REC | Alarma Baja Presión Por Transductor Circ Recup. | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"LP by transducer alarm recovery circuit"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma Baja Presión Por Transductor Circ Recup."}}} | [] | modbus
693 | 146 | Al_Probe08 | Alarma sonda Temperatura Descarga 1 (0-No alarma 1-Alarma) | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Supply temperature 1 probe alarm (0-No alarm 1-Alarm)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma sonda Temperatura Descarga 1 (0-No alarma 1-Alarma)"}}} | [] | modbus
694 | 148 | Al_Probe07 | Alarma Sonda Presión Evaporación Circuito 1 (0-No alarma 1- | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Evaporation preassure circuit 1 probe alarm (0-No alarm 1-A"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma Sonda Presión Evaporación Circuito 1 (0-No alarma 1-"}}} | [] | modbus
695 | 150 | VENT_AIRE_RET_TN | Paro/Marcha Ventilador Aire Retorno | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Return fan stop/start"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Paro/Marcha Ventilador Aire Retorno"}}} | [] | modbus
696 | 151 | Al_Probe24 | Alarma Sonda Desconectada O Estropeada Presión Evaporación C | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Evaporation pressure probe circuit 2 fault or not connected "},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma Sonda Desconectada O Estropeada Presión Evaporación C"}}} | [] | modbus
697 | 153 | En_Energy_management | Habilitar Control Demanda | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Enable control demand"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Habilitar Control Demanda"}}} | [] | modbus
698 | 154 | AVISO_Texterior_BAJA_PARO_COMPRE | Aviso Temperatura Exterior Baja Bloqueo Funcionamiento Compr | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Working compressors block low external temperature warning"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Aviso Temperatura Exterior Baja Bloqueo Funcionamiento Compr"}}} | [] | modbus
699 | 156 | Al_Probe_T_Ret | Alarma Sonda Desconectada O Estropeada Temperatura Retorno A | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Air return temperature probe fault or not connected (0-No al"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma Sonda Desconectada O Estropeada Temperatura Retorno A"}}} | [] | modbus
700 | 157 | Al_Probe_H_Ret | Alarma Sonda Desconectada O Estropeada Humedad Retorno Aire | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Air return humidity probe fault or not connected (0-No alarm"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma Sonda Desconectada O Estropeada Humedad Retorno Aire"}}} | [] | modbus
701 | 158 | mID_AL_FILTRO | Status Of The Boolean Input (0: Contact Closed, 1: Contact O | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Status of the Boolean input (0: contact closed, 1: contact o"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Status Of The Boolean Input (0: Contact Closed, 1: Contact O"}}} | [] | modbus
702 | 159 | W_FILTRO | Aviso Filtro Sucio | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Filter warning"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Aviso Filtro Sucio"}}} | [] | modbus
703 | 160 | ETAPA_POST_CALEN_1 | Etapa 1 Bateria Postcalentamiento | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Post-coil stage 1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Etapa 1 Bateria Postcalentamiento"}}} | [] | modbus
704 | 161 | ETAPA_POST_CALEN_2 | Etapa 2 Bateria Postcalentamiento | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Post-coil stage 2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Etapa 2 Bateria Postcalentamiento"}}} | [] | modbus
705 | 162 | ETAPA_R_PRECAL_1 | Etapa 1 Bateria Precalentamiento | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Pre-coil stage 1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Etapa 1 Bateria Precalentamiento"}}} | [] | modbus
706 | 163 | ETAPA_R_PRECAL_2 | Etapa 2 Bateria Precalentamiento | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Pre-coil stage 2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Etapa 2 Bateria Precalentamiento"}}} | [] | modbus
707 | 164 | mID_AL_FUGA_REFRI | Detector De Fuga Refrigerante | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Leaks detector"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Detector De Fuga Refrigerante"}}} | [] | modbus
708 | 165 | Al_Probe_Pr_I_R | Alarma Sonda Desconectada O Estropeada Presion Diferencial | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Differential pressure probe fault or not connected (0-No ala"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma Sonda Desconectada O Estropeada Presion Diferencial"}}} | [] | modbus
709 | 166 | En_GLOBAL_Humedad | Habilita Global Humedad (Cuando hay maestro y esclavo ) | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Enable global humidity (When there are master and slave )"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Habilita Global Humedad (Cuando hay maestro y esclavo )"}}} | [] | modbus
710 | 168 | PERMISO_SECAR | Permiso Secar Humedad, habilitar deshumectación | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Humidity dry permission, enable dehumidification"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Permiso Secar Humedad, habilitar deshumectación"}}} | [] | modbus
711 | 169 | ACTIVO_GLOBAL | Habilitar la opción de placa maestra, desde PGD (Cuando hay | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Enable master board option, from PGD (When master and slave)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Habilitar la opción de placa maestra, desde PGD (Cuando hay"}}} | [] | modbus
712 | 171 | Al_Present_NIC_Ret | Alarma presente en ventilador Retorno Nicotra (0-No alarma 1 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Alarm present on fan Nicotra Return (0-No alarm 1-Alarm)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma presente en ventilador Retorno Nicotra (0-No alarma 1"}}} | [] | modbus
713 | 172 | Al_Offline_NIC_Ret | Alarma: Offline ventilador Retorno Nicotra (0-No alarma 1-Al | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Alarm: Offline Nicotra Return Fan (0-No Alarm 1-Alarm)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma: Offline ventilador Retorno Nicotra (0-No alarma 1-Al"}}} | [] | modbus
714 | 173 | Comp1_Circ2 | Estado Compresor1 circuito2 (0: Off; 1: On) si este se encu | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Compressor1 circuit2 (0: Off; 1: On)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Estado Compresor1 circuito2 (0: Off; 1: On) si este se encu"}}} | [] | modbus
715 | 174 | Comp1_Circ3 | Estado Compresor1 circuito3 (0: Off; 1: On) si este se encu | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Compressor1 circuit3 (0: Off; 1: On)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Estado Compresor1 circuito3 (0: Off; 1: On) si este se encu"}}} | [] | modbus
716 | 175 | Comp2_Circ3 | Estado Compresor2 circuito3 (0: Off; 1: On) si este se encu | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Compressor2 circuit3 (0: Off; 1: On)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Estado Compresor2 circuito3 (0: Off; 1: On) si este se encu"}}} | [] | modbus
717 | 176 | Comp3_Circ3 | Estado Compresor3 circuito3 (0: Off; 1: On) si este se encu | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Compressor3 circuit3 (0: Off; 1: On)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Estado Compresor3 circuito3 (0: Off; 1: On) si este se encu"}}} | [] | modbus
718 | 177 | Comp1_Circ4 | Estado Compresor1 circuito4 (0: Off; 1: On) si este se encue | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Compressor1 circuit4 (0: Off; 1: On)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Estado Compresor1 circuito4 (0: Off; 1: On) si este se encue"}}} | [] | modbus
719 | 178 | Comp2_Circ4 | Estado Compresor2 circuito4 (0: Off; 1: On) si este se encue | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Compressor2 circuit4 (0: Off; 1: On)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Estado Compresor2 circuito4 (0: Off; 1: On) si este se encue"}}} | [] | modbus
720 | 179 | Comp3_Circ4 | Estado Compresor3 circuito4 (0: Off; 1: On) si este se encu | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Compressor3 circuit4 (0: Off; 1: On)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Estado Compresor3 circuito4 (0: Off; 1: On) si este se encu"}}} | [] | modbus
721 | 229 | SET_DAY | Establecer nuevo día | CLOCK / TIMEDATE |  | simple | 0 | 3 | 6 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Request to copy NEW_DAY into DAY"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Establecer nuevo día"}}} | [] | modbus
722 | 230 | SET_HOUR | Establecer nueva hora | CLOCK / TIMEDATE |  | simple | 0 | 3 | 6 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Request to copy NEW_HOUR into HOUR"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Establecer nueva hora"}}} | [] | modbus
723 | 231 | SET_MINUTE | Establecer nuevo minuto | CLOCK / TIMEDATE |  | simple | 0 | 3 | 6 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Request to copy NEW_MINUTE into MINUTE"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Establecer nuevo minuto"}}} | [] | modbus
724 | 232 | SET_MONTH | Establecer nuevo mes | CLOCK / TIMEDATE |  | simple | 0 | 3 | 6 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Request to copy NEW_MONTH into MONTH"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Establecer nuevo mes"}}} | [] | modbus
725 | 233 | SET_WEEKDAY | Establecer nuevo día de la semana | CLOCK / TIMEDATE |  | simple | 0 | 3 | 6 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Request to copy NEW_WEEKDAY into WEEKDAY"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Establecer nuevo día de la semana"}}} | [] | modbus
726 | 234 | SET_YEAR | Establecer nuevo año | CLOCK / TIMEDATE |  | simple | 0 | 3 | 6 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Request to copy NEW_YEAR into YEAR"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Establecer nuevo año"}}} | [] | modbus
727 | 235 | En_DST | Habilitar Cambio Horario (0-Deshabilitado; 1- Habilitado) | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Enabling the Time Shift Enable (0-Disabled; 1- Enabled)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Habilitar Cambio Horario (0-Deshabilitado; 1- Habilitado)"}}} | [] | modbus
728 | 236 | Online_Imp_NIC | Impulsión Nicotra online | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Online supply Nicotra"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Impulsión Nicotra online"}}} | [] | modbus
729 | 237 | Al_Offline_NIC_Imp | Alarma: Offline ventilador Impulsion Nicotra (0-No alarma 1- | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Alarm: Offline Nicotra Supply Fan (0-No Alarm 1-Alarm)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma: Offline ventilador Impulsion Nicotra (0-No alarma 1-"}}} | [] | modbus
730 | 238 | Online_Ret_NIC | Retorno Nicotra online | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Online return Nicotra"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Retorno Nicotra online"}}} | [] | modbus
731 | 239 | Al_Present_NIC_Imp | Alarma en Ventilador Impulsion Nicotra (0-No alarma 1-Alarma | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Nicotra Supply Fan Alarm (0-No Alarm 1-Alarm)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma en Ventilador Impulsion Nicotra (0-No alarma 1-Alarma"}}} | [] | modbus
732 | 240 | En_Superv_OnOff | Habilitar supervisión | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Enable supervision"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Habilitar supervisión"}}} | [] | modbus
733 | 241 | PRIORIDAD_PM_REMOTO | Prioridad Paro/Marcha remoto | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Remote stop/start priority"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Prioridad Paro/Marcha remoto"}}} | [] | modbus
734 | 242 | PRIORIDAD_SUPERVISION | Prioridad Paro/Marcha supervisión | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Supervision stop/start priority"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Prioridad Paro/Marcha supervisión"}}} | [] | modbus
735 | 243 | EST_DESESCARCHE_CIRC1 | Estado desescarche circuito 1 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Defrost circuit 1 status"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Estado desescarche circuito 1"}}} | [] | modbus
736 | 244 | EST_DESESCARCHE_CIRC2 | Estado desescarche circuito 2 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Defrost circuit 2 status"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Estado desescarche circuito 2"}}} | [] | modbus
737 | 245 | EST_DESESCARCHE_CIRC_REC | Estado desescarche circuito recuperación | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Defrost recovery circuit status"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Estado desescarche circuito recuperación"}}} | [] | modbus
738 | 246 | INV_VER_PANTALLA | Estado Invierno/Verano | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Cooling / Heating status"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Estado Invierno/Verano"}}} | [] | modbus
739 | 247 | EST_DESESCARCHE_CIRC3 | Estado desescarche circuito 3 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Defrost circuit 4 status"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Estado desescarche circuito 3"}}} | [] | modbus
740 | 264 | Prior_Confort | Antepone conservar la temperatura a bajar el CO2 | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Dampers limits setting Mixing temp."},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Antepone conservar la temperatura a bajar el CO2"}}} | [] | modbus
741 | 265 | mAl_Probe01 | Memoria Alarma temperatura exterior | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"External temperature"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Memoria Alarma temperatura exterior"}}} | [] | modbus
742 | 266 | mAl_Probe02 | Memoria temperatura retorno / ambiente | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Return / Ambient temperature"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Memoria temperatura retorno / ambiente"}}} | [] | modbus
743 | 267 | mAl_Probe03 | Memoria Alarma temperatura mezcla | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Mixing temperature"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Memoria Alarma temperatura mezcla"}}} | [] | modbus
744 | 268 | mAl_Probe04 | Memoria Alarma temperatura impulsión | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Supply temperature"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Memoria Alarma temperatura impulsión"}}} | [] | modbus
745 | 269 | mAl_Probe05 | Memoria Alarma humedad exterior | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"External humidity"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Memoria Alarma humedad exterior"}}} | [] | modbus
746 | 270 | mAl_Probe05_T | Memoria Alarma temperatura aspiracion 1 | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Supply temperature 1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Memoria Alarma temperatura aspiracion 1"}}} | [] | modbus
747 | 271 | mAl_Probe06 | Memoria Alarma presión condensación circuito 1 | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Condensation pressure circuit 1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Memoria Alarma presión condensación circuito 1"}}} | [] | modbus
748 | 272 | mAl_Probe07 | Memoria Alarma presion evaporacion 1 | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Evaporation pressure 1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Memoria Alarma presion evaporacion 1"}}} | [] | modbus
749 | 273 | mAl_Probe08 | Memoria Alarma temperatura descarga 1 | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Discharge temperature 1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Memoria Alarma temperatura descarga 1"}}} | [] | modbus
750 | 274 | mAl_Probe09 | Memoria Alarma temperatura aspiracion | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Suction temperature"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Memoria Alarma temperatura aspiracion"}}} | [] | modbus
751 | 275 | mAl_Probe10 | Memoria Alarma CO2 | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"CO2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Memoria Alarma CO2"}}} | [] | modbus
752 | 276 | mAl_Probe11 | Memoria Alarma VOC | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"VOC"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Memoria Alarma VOC"}}} | [] | modbus
753 | 277 | mAl_Probe12 | Memoria Alarma humedad interior | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Internal humidity"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Memoria Alarma humedad interior"}}} | [] | modbus
754 | 304 | Warning_LP_Pressostat | Aviso presostato baja | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"LP warning status by pressostat"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Aviso presostato baja"}}} | [] | modbus
755 | 305 | Warning_LP_Transducer | Aviso transductor baja | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"LP warning status by transducer"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Aviso transductor baja"}}} | [] | modbus
756 | 306 | mAL_TERM_VENT_INTERIOR | Alarma térmico ventilador interior | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Overload compressor internal fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma térmico ventilador interior"}}} | [] | modbus
757 | 307 | mAL_DESESCAR_X_TIEMPO | Alarma finaliza desescarche por tiempo | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Defrost end time alarm"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma finaliza desescarche por tiempo"}}} | [] | modbus
758 | 311 | mAl_Temperature_Probe | Alarma THTune sonda temperatura usada | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Alarm on the THTune temperature probe actually used"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma THTune sonda temperatura usada"}}} | [] | modbus
759 | 312 | mAl_Humidity_Probe | Alarma THTune sonda humedad | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Alarm on the THTune humidity probe"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma THTune sonda humedad"}}} | [] | modbus
760 | 313 | mAl_Clock_Board | Alarma THTune tarjeta reloj | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Alarm on the THTune clock board"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma THTune tarjeta reloj"}}} | [] | modbus
761 | 314 | mAlarm_Grave_HP_Pressostat | Alarma presostato de alta modo manual | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"HP by pressostat work in manual reset mode"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma presostato de alta modo manual"}}} | [] | modbus
762 | 315 | mAlarm_Grave_HP_Transducer | Alarma transductor de alta modo manual | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"HP by transducer work in manual reset mode"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma transductor de alta modo manual"}}} | [] | modbus
763 | 335 | Warning_Estado | Alarma Ventilador Impulsión aviso Fallo Estado (0-No Alarma; | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Suply Fan Alarm Warning Fault Status (0-No Alarm; 1- Alarm)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma Ventilador Impulsión aviso Fallo Estado (0-No Alarma;"}}} | [] | modbus
764 | 337 | mAl_Intensida_Maxima | Alarma intensidad máxima superada, con medidor de energía | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Maximun current limit alarm with energy meter"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma intensidad máxima superada, con medidor de energía"}}} | [] | modbus
765 | 338 | mAl_Potencia_Maxima | Alarma potencia máxima superada, con medidor de energía | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Maximun power limit alarm with energy meter"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma potencia máxima superada, con medidor de energía"}}} | [] | modbus
766 | 340 | mWarningPresent_EBM | Aviso de Ventilador EBM (0-No aviso; 1- Aviso) | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"EBM Fan Warning (0-No warning; 1- Warning)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Aviso de Ventilador EBM (0-No aviso; 1- Aviso)"}}} | [] | modbus
767 | 343 | mAlrm_Caudal_Int | Alarma caudal impulsión | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Air flow supply lack"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma caudal impulsión"}}} | [] | modbus
768 | 344 | mAlrm_Caudal_Ret | Alarma caudal retorno | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Air flow return lack"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma caudal retorno"}}} | [] | modbus
769 | 345 | mID_AL_ANTIFREEZE_COIL | Alarma Quemador / Resistencia | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Anti-freeze coil alarm"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma Quemador / Resistencia"}}} | [] | modbus
770 | 346 | mID_AL_RECUP_ROT | Alarma Quemador / Resistencia | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Anti-freeze coil alarm"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma Quemador / Resistencia"}}} | [] | modbus
771 | 347 | AL_COM_GLOBAL | Alarma por No comunicación con la Placa Maestra (0-No Alar | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Alarm for No Communication with Master Board (0-No Alarm; 1-"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma por No comunicación con la Placa Maestra (0-No Alar"}}} | [] | modbus
772 | 348 | mFuga_C1 | Alarma de posible fuga de Refrigerante Circuito 1 (0-No Alar | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Possible Refrigerant Leakage Alarm Circuit 1 (0-No Alarm; 1-"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma de posible fuga de Refrigerante Circuito 1 (0-No Alar"}}} | [] | modbus
773 | 349 | mFuga_C2 | Alarma de posible fuga de Refrigerante Circuito 2 (0-No Alar | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Possible Refrigerant Leakage Alarm Circuit 2 (0-No Alarm; 1-"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma de posible fuga de Refrigerante Circuito 2 (0-No Alar"}}} | [] | modbus
774 | 350 | mFuga_C3 | Alarma de posible fuga de Refrigerante Circuito 3 (0-No Alar | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Possible Refrigerant Leakage Alarm Circuit 3 (0-No Alarm; 1-"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma de posible fuga de Refrigerante Circuito 3 (0-No Alar"}}} | [] | modbus
775 | 351 | mFuga_CR | Alarma de posible fuga de Refrigerante Circuito Recuperacion | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Possible Refrigerant Leak in Recovery Circuit Alarm (0-No Al"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma de posible fuga de Refrigerante Circuito Recuperacion"}}} | [] | modbus
776 | 358 | mAlarma_V_Retorno | Alarma ventilador retorno | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Return fan alarm"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma ventilador retorno"}}} | [] | modbus
777 | 359 | mAl_Offline_EBM | Alarma ventilador EBM offline | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Offline alarm memory for Ebmpapst fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma ventilador EBM offline"}}} | [] | modbus
778 | 364 | mAl_Seriales | Alarma sondas seriales desconectadas (0-No Alarma; 1- Alarma | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Serial probes disconnected alarm (0-No Alarm; 1- Alarm)"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma sondas seriales desconectadas (0-No Alarma; 1- Alarma"}}} | [] | modbus
779 | 365 | mID_EMERGENCIA | Paro de emergencia | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Emergency stop"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Paro de emergencia"}}} | [] | modbus
780 | 366 | mID_AL_HUMIDIFICADOR | Alarma humidificador | ALARM |  | simple | 30 | 3 | 6 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Humidifier alarm"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma humidificador"}}} | [] | modbus
781 | 367 | mID_AL_QUEMA_RESIST | Alarma quemador / resistencia | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Elect.Heater/Burner alarm"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma quemador / resistencia"}}} | [] | modbus
782 | 372 | CPCOE.Or_Probe_Alarms | Alarma sonda procedente del modulo de expansion | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Probe alarm coming from the expansion module"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma sonda procedente del modulo de expansion"}}} | [] | modbus
783 | 390 | mAl_P_DIF_IMP_RET | Alarma superado límite de presión diferencial de impulsión / | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Supply / return differ. pressure limit reached alarm"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma superado límite de presión diferencial de impulsión /"}}} | [] | modbus
784 | 391 | HP_Prevent_Cric1 | High pressure prevent warning | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"High pressure prevent warning"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"High pressure prevent warning"}}} | [] | modbus
785 | 392 | LP_Prevent_Circ1 | Low pressure prevent warning | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Low pressure prevent warning"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Low pressure prevent warning"}}} | [] | modbus
786 | 393 | Disc_Low_Prevent_Circ1 | Circuit 1 Warning Discharge low prevent | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Circuit 1 Warning Discharge low prevent"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Circuit 1 Warning Discharge low prevent"}}} | [] | modbus
787 | 394 | Disc_High_Prevent_Circ1 | Circuit 1 Warning Discharge high prevent | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Circuit 1 Warning Discharge high prevent"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Circuit 1 Warning Discharge high prevent"}}} | [] | modbus
788 | 395 | mDisc_High_Alarm_Circ1 | Alcanzado nivel alarma temperatura descarga circuito 1 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Discharge temperature alarm level reached circuit 1"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alcanzado nivel alarma temperatura descarga circuito 1"}}} | [] | modbus
789 | 396 | mDisc_High_Alarm_Circ2 | Alcanzado nivel alarma temperatura descarga circuito 2 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Discharge temperature alarm level reached circuit 2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alcanzado nivel alarma temperatura descarga circuito 2"}}} | [] | modbus
790 | 397 | mDisc_High_Alarm_Circ3 | Alcanzado nivel alarma temperatura descarga circuito 3 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Discharge temperature alarm level reached circuit 3"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alcanzado nivel alarma temperatura descarga circuito 3"}}} | [] | modbus
791 | 398 | mDisc_High_Alarm_CircR | Alcanzado nivel alarma temperatura descarga circuito recuper | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Discharge temperature alarm level reached recovery circuit"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alcanzado nivel alarma temperatura descarga circuito recuper"}}} | [] | modbus
792 | 399 | HP_Prevent_Cric2 | Aviso presión alta circuito 2 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"High pressure prevent warning circuit 2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Aviso presión alta circuito 2"}}} | [] | modbus
793 | 400 | LP_Prevent_Circ2 | Aviso presión baja circuito 2 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Low pressure prevent warning circuit 2"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Aviso presión baja circuito 2"}}} | [] | modbus
794 | 401 | Disc_Low_Prevent_Circ2 | Aviso baja descarga circuito 2 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Circuit 2 Warning Discharge low prevent"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Aviso baja descarga circuito 2"}}} | [] | modbus
795 | 402 | Disc_High_Prevent_Circ2 | Aviso alta descarga circuito 2 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Circuit 2 Warning Discharge high prevent"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Aviso alta descarga circuito 2"}}} | [] | modbus
796 | 403 | HP_Prevent_Cric3 | Aviso presión alta circuito 3 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"High pressure prevent warning circuit 3"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Aviso presión alta circuito 3"}}} | [] | modbus
797 | 404 | LP_Prevent_Circ3 | Aviso presión baja circuito 3 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Low pressure prevent warning circuit 3"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Aviso presión baja circuito 3"}}} | [] | modbus
798 | 405 | Disc_Low_Prevent_Circ3 | Aviso baja descarga circuito 3 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Circuit 3 Warning Discharge low prevent"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Aviso baja descarga circuito 3"}}} | [] | modbus
799 | 406 | Disc_High_Prevent_Circ3 | Aviso alta descarga circuito 3 | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Circuit 3 Warning Discharge high prevent"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Aviso alta descarga circuito 3"}}} | [] | modbus
800 | 407 | EDV_1.OR_Reg_Alarms_Vlv_A | Alarmas regulación circuito 1 en driver | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Regulation alarms circuit 1 en driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarmas regulación circuito 1 en driver"}}} | [] | modbus
801 | 408 | EDV_1.D8_EEV_ALARM_ui | EEV error motor circuito 1 en driver | ALARM |  | simple | 30 | 3 | 6 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"EEV motor error - circuit 1 from driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"EEV error motor circuito 1 en driver"}}} | [] | modbus
802 | 409 | EDV_1.D10_LOP_ALARM_ui | LOP alarma circuito 1 en driver | ALARM |  | simple | 30 | 3 | 6 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"LOP alarm - circuit 1 from driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"LOP alarma circuito 1 en driver"}}} | [] | modbus
803 | 410 | EDV_1.D12_LOW_SH_ALARM_ui | LowSH alarma circuito 1 en driver | ALARM |  | simple | 30 | 3 | 6 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"LowSH (low super heat) alarm - circuit 1 from driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"LowSH alarma circuito 1 en driver"}}} | [] | modbus
804 | 411 | EDV_1.D1_LOW_SUCT_ALARM_ui | Baja temperatura aspiración alarma circuito 1 en driver | ALARM |  | simple | 30 | 3 | 6 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Low suction temperature alarm - circuit 1 from driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Baja temperatura aspiración alarma circuito 1 en driver"}}} | [] | modbus
805 | 412 | EDV_1.D13_HITCOND_ALARM_ui | Alta temperatura aspiración alarma circuito 1 en driver | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"High suction temperature alarm - circuit 1 from driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alta temperatura aspiración alarma circuito 1 en driver"}}} | [] | modbus
806 | 413 | EDV_1.OR_Reg_Alarms_Vlv_B | Alarmas regulación circuito 2 en driver | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Regulation alarms circuit 2 from driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarmas regulación circuito 2 en driver"}}} | [] | modbus
807 | 414 | EDV_1.D30_EEV_ALARM_2ND_ui | EEV error motor circuito 2 en driver | ALARM |  | simple | 30 | 3 | 6 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"EEV motor error -circuit 2 from driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"EEV error motor circuito 2 en driver"}}} | [] | modbus
808 | 415 | EDV_1.D28_MOP_ALARM_2ND_ui | MOP alarma circuito 2 en driver | ALARM |  | simple | 30 | 3 | 6 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"MOP alarm - circuit 2 from driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"MOP alarma circuito 2 en driver"}}} | [] | modbus
809 | 416 | EDV_1.D26_LOW_SH_ALARM_2ND_ui | LowSH alarma circuito 2 en driver | ALARM |  | simple | 30 | 3 | 6 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"LowSH (low super heat) alarm - circuit 2 from driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"LowSH alarma circuito 2 en driver"}}} | [] | modbus
810 | 417 | EDV_1.D29_LOW_SUCT_ALARM_2ND_ui | Baja temperatura aspiración alarma circuito 2 en driver | ALARM |  | simple | 30 | 3 | 6 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Low suction temperature alarm - circuit 2 from driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Baja temperatura aspiración alarma circuito 2 en driver"}}} | [] | modbus
811 | 418 | EDV_1.OR_System_Alarms | Alarmas sistema en driver | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"System alarms from driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarmas sistema en driver"}}} | [] | modbus
812 | 420 | EDV_1.D4_S1_Alarm_ui | Alarma sonda S1 en driver | ALARM |  | simple | 30 | 3 | 6 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Alarm probe S1 from driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma sonda S1 en driver"}}} | [] | modbus
813 | 421 | EDV_1.D5_S2_Alarm_ui | Alarma sonda S2 en driver | ALARM |  | simple | 30 | 3 | 6 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Alarm probe S2 from driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma sonda S2 en driver"}}} | [] | modbus
814 | 422 | EDV_1.D6_S3_Alarm_ui | Alarma sonda S3 en driver | ALARM |  | simple | 30 | 3 | 6 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Alarm probe S3 from driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma sonda S3 en driver"}}} | [] | modbus
815 | 423 | EDV_1.D7_S4_Alarm_ui | Alarma sonda S4 en driver | ALARM |  | simple | 30 | 3 | 6 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Alarm probe S4 from driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma sonda S4 en driver"}}} | [] | modbus
816 | 424 | EDV_1.D25_BATTERY_ALARM_ui | Alarma descarga batería Driver | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Discharge battery alarm from driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma descarga batería Driver"}}} | [] | modbus
817 | 425 | EDV_1.EVD_Al_Offline_ui | EVD offline alarma | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"EVD offline alarm"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"EVD offline alarma"}}} | [] | modbus
818 | 426 | Configuration_Error | Error transmisión de parámetros | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Parameters transmission error"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Error transmisión de parámetros"}}} | [] | modbus
819 | 427 | FW_Compatibility_Error | Firmware no compatible / incapaz de comunicar con el EVD EVO | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"The fw in the EVDEVO connected is not compatible with the mo"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Firmware no compatible / incapaz de comunicar con el EVD EVO"}}} | [] | modbus
820 | 434 | EDV_2.D11_MOP_ALARM_ui | MOP alarma - cricuito 3 en driver | ALARM |  | simple | 30 | 3 | 6 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"MOP alarm - circuit 3 in driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"MOP alarma - cricuito 3 en driver"}}} | [] | modbus
821 | 439 | EDV_2.D27_LOP_ALARM_2ND_ui | LOP alarma - circuito 4 en driver | ALARM |  | simple | 30 | 3 | 6 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"LOP alarm - circuit 4 in driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"LOP alarma - circuito 4 en driver"}}} | [] | modbus
822 | 454 | OR_LOW_SH_ALARM | Alarmas sobrecalentamiento bajo en placa | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Low superheating alarms on board"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarmas sobrecalentamiento bajo en placa"}}} | [] | modbus
823 | 455 | mAL_D12_LOW_SH_ALARM | LowSH alarma - circuito 1 en placa | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"LowSH (low super heat) alarm -circuit 1 on board"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"LowSH alarma - circuito 1 en placa"}}} | [] | modbus
824 | 456 | mAL_D26_LOW_SH_ALARM_2ND | LowSH alarma - circuito 2 en placa | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"LowSH (low super heat) alarm - circuit 2 on board"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"LowSH alarma - circuito 2 en placa"}}} | [] | modbus
825 | 457 | OR_LOP_ALARM | Alarmas LOP en placa | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"LOP alarms onboard"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarmas LOP en placa"}}} | [] | modbus
826 | 458 | mAL_D10_LOP_ALARM | Alarma por Baja Tempera de Evaporación - circuito 1 en placa | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Low Evaporation Temperature Alarm - circuit 1 on board"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma por Baja Tempera de Evaporación - circuito 1 en placa"}}} | [] | modbus
827 | 459 | mAL_D27_LOP_ALARM_2ND | Alarma por Baja Tempera de Evaporación - circuito 2 en placa | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Low Evaporation Temperature Alarm - circuit 2 on board"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma por Baja Tempera de Evaporación - circuito 2 en placa"}}} | [] | modbus
828 | 460 | OR_MOP_ALARM | Alarmas MOP en placca | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"MOP Alarms"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarmas MOP en placca"}}} | [] | modbus
829 | 461 | mAL_D11_MOP_ALARM | MOP alarma - circuito 1 en placa | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"MOP alarm - circuit 1 on board"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"MOP alarma - circuito 1 en placa"}}} | [] | modbus
830 | 462 | mAL_D28_MOP_ALARM_2ND | MOP alarma - circuito 2 en placa | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"MOP alarm - circuit 2 on board"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"MOP alarma - circuito 2 en placa"}}} | [] | modbus
831 | 463 | msk_D13_HITCOND_ALARM | Alta temperatura condensación en placa | ALARM |  | simple | 30 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 1bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"High condensation temperature on board"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alta temperatura condensación en placa"}}} | [] | modbus
832 | 464 | OR_LOW_SUCT_ALARM | Alarmas baja temperatura aspiración en placa | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Low suction temperatures alarms on board"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarmas baja temperatura aspiración en placa"}}} | [] | modbus
833 | 465 | mAL_D1_LOW_SUCT_ALARM | Baja temperatura aspiración alarma -circuito 1 en placa | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Low temperature suction alarm -circuit 1 on board"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Baja temperatura aspiración alarma -circuito 1 en placa"}}} | [] | modbus
834 | 466 | mAL_D29_LOW_SUCT_ALARM_2ND | Baja temperatura aspiración alarma - circuito 2 en placa | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Low temperature suction alarm - circuit 2 on board"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Baja temperatura aspiración alarma - circuito 2 en placa"}}} | [] | modbus
835 | 468 | mAL_D40_EVOTUNES_ALARM | Self-tuning alarma - circuito 1 en placa | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Memory alarm - Self-tuning alarm circuit 1 on board"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Self-tuning alarma - circuito 1 en placa"}}} | [] | modbus
836 | 469 | mAL_D42_EVOTUNES_ALARM_2ND | Self-tuning alarma -circuito 2 en placa | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Memory alarm - Self-tuning alarm circuit 2 on board"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Self-tuning alarma -circuito 2 en placa"}}} | [] | modbus
837 | 471 | mAl_Offline_cpCOe | Offline alarma - cpCOe | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Offline alarm - cpCOe"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Offline alarma - cpCOe"}}} | [] | modbus
838 | 472 | mAl_CfgErr | Offline alarma - cpCOe | CONFIG_PARAMETER |  | simple | 0 | 1 | 5 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Offline alarm - cpCOe"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Offline alarma - cpCOe"}}} | [] | modbus
839 | 501 | Al_Present_ZA_Imp | Alarma presente ventilador Zhiel-Abegg | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Alarm is present for the Zhiel-Abegg fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma presente ventilador Zhiel-Abegg"}}} | [] | modbus
840 | 502 | Al_Present2_Imp_ZA | Alarma presente ventilador Zhiel-Abegg | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"alarm is present for the Zhiel-Abegg fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma presente ventilador Zhiel-Abegg"}}} | [] | modbus
841 | 503 | Al_Present_ZA_Ret | Alarma presente ventilador Zhiel-Abegg | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Alarm is present for the Zhiel-Abegg fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma presente ventilador Zhiel-Abegg"}}} | [] | modbus
842 | 504 | Al_Present2_Ret_ZA | alarma presente ventilador Zhiel-Abegg | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Alarm is present for the Zhiel-Abegg fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"alarma presente ventilador Zhiel-Abegg"}}} | [] | modbus
843 | 505 | mAl_Offline_ZA | Offline alarma - ventilador Ziehl-Abegg | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Offline alarm - Ziehl-Abegg fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Offline alarma - ventilador Ziehl-Abegg"}}} | [] | modbus
844 | 507 | mAl_Present_ZA | Alarma presente ventilador Zhiel-Abegg | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Alarm is present in the Zhiel-Abegg fan"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Alarma presente ventilador Zhiel-Abegg"}}} | [] | modbus
845 | 509 | EDV_1.D14_DIGIN1_STATUS_msk | DI1 estado proveniente Driver | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"DI1 status from Driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"DI1 estado proveniente Driver"}}} | [] | modbus
846 | 510 | EDV_1.D15_DIGIN2_STATUS_msk | DI2 estado proveniente Driver | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"DI2 status from Driver"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"DI2 estado proveniente Driver"}}} | [] | modbus
847 | 514 | BombaCalor_o_Cooling | Estado Invierno / Verano | CONFIG_PARAMETER |  | simple | 0 | 4 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 16bit |  | {"severity":"none"} | [] | {"_type":"l10n","default_lang":"es_ES","translations":{"en_US":{"name":null,"_type":"languages","category":null,"description":"Cooling / Heating Status"},"es_ES":{"name":null,"_type":"languages","category":null,"description":"Estado Invierno / Verano"}}} | [] | modbus